## BOQ
BILL OF QUANTITIES - HVAC (QUANTITIES ONLY, NO PRICES) - Sample Villa - Riyadh
PRELIMINARY DESIGN - FOR COORDINATION ONLY. To be checked and stamped by a qualified HVAC engineer before construction.
Location: Riyadh, Saudi Arabia Codes: Saudi Building Code + ASHRAE Units: SI
Item No. | Description | Specification | Unit | Quantity | Waste % | Qty incl. allowance | Floor/Zone | Remarks
A. HVAC EQUIPMENT
A.1 | Wall-mounted split indoor unit | WS-18: 5.3 kW nominal cooling, 250 L/s, ESP 0 Pa, heat 5.6 kW, R410A | No. | 1 | 0 |  | Z-GF-01 | Tags: IU-GF-01
A.2 | Wall-mounted split indoor unit | WS-09: 2.6 kW nominal cooling, 140 L/s, ESP 0 Pa, heat 2.9 kW, R410A | No. | 1 | 0 |  | Z-GF-02 | Tags: IU-GF-02
A.3 | Through-wall fresh air fan with G4 filter and weather hood | FAF-15: 8 L/s, 12 W | No. | 1 | 0 |  | Z-GF-02 | Tags: FAF-GF-02
A.4 | Ducted split indoor unit (concealed) | DS-24: 7.0 kW nominal cooling, 380 L/s, ESP 75 Pa, heat 7.6 kW, R410A | No. | 1 | 0 |  | Z-GF-03 | Tags: IU-GF-03
A.5 | Ducted split indoor unit (concealed) | DS-48: 14.0 kW nominal cooling, 750 L/s, ESP 100 Pa, heat 15.0 kW, R410A | No. | 1 | 0 |  | Z-GF-04 | Tags: IU-GF-04
A.6 | Ducted split indoor unit (concealed) | DS-18: 5.3 kW nominal cooling, 300 L/s, ESP 75 Pa, heat 5.8 kW, R410A | No. | 1 | 0 |  | Z-FF-01 | Tags: IU-FF-01
A.7 | Ducted split indoor unit (concealed) | DS-48: 14.0 kW nominal cooling, 750 L/s, ESP 100 Pa, heat 15.0 kW, R410A | No. | 1 | 0 |  | Z-FF-02 | Tags: IU-FF-02
A.8 | Outdoor condensing unit (heat pump) | WS-O-18: 5.3 kW nominal, 1.61 kW input, T3 rated, anti-vibration mounts | No. | 1 | 0 |  | RF | Tags: ODU-01
A.9 | Outdoor condensing unit (heat pump) | WS-O-09: 2.6 kW nominal, 0.76 kW input, T3 rated, anti-vibration mounts | No. | 1 | 0 |  | RF | Tags: ODU-02
A.10 | Outdoor condensing unit (heat pump) | DS-O-24: 7.0 kW nominal, 2.19 kW input, T3 rated, anti-vibration mounts | No. | 1 | 0 |  | RF | Tags: ODU-03
A.11 | Outdoor condensing unit (heat pump) | DS-O-48: 14.0 kW nominal, 4.52 kW input, T3 rated, anti-vibration mounts | No. | 1 | 0 |  | RF | Tags: ODU-04
A.12 | Outdoor condensing unit (heat pump) | DS-O-18: 5.3 kW nominal, 1.66 kW input, T3 rated, anti-vibration mounts | No. | 1 | 0 |  | RF | Tags: ODU-05
A.13 | Outdoor condensing unit (heat pump) | DS-O-48: 14.0 kW nominal, 4.52 kW input, T3 rated, anti-vibration mounts | No. | 1 | 0 |  | RF | Tags: ODU-06
B. GALVANISED STEEL DUCTWORK (SMACNA)
B.1 | Galvanised sheet steel rectangular duct incl. fittings, joints, sealant | 22 ga (0.85 mm), low pressure (500 Pa) class, Seal class A | m² | 2.76 | 10 |  | FF
B.2 | Galvanised sheet steel rectangular duct incl. fittings, joints, sealant | 24 ga (0.70 mm), low pressure (500 Pa) class, Seal class A | m² | 4.12 | 10 |  | FF
B.3 | Galvanised sheet steel rectangular duct incl. fittings, joints, sealant | 26 ga (0.55 mm), low pressure (500 Pa) class, Seal class A | m² | 24.81 | 10 |  | FF
B.4 | Galvanised sheet steel round spiral duct incl. fittings, joints, sealant | 26 ga (0.55 mm), low pressure (500 Pa) class, Seal class A | m² | 14.83 | 10 |  | FF
B.5 | Galvanised sheet steel rectangular duct incl. fittings, joints, sealant | 22 ga (0.85 mm), low pressure (500 Pa) class, Seal class A | m² | 2.76 | 10 |  | GF
B.6 | Galvanised sheet steel rectangular duct incl. fittings, joints, sealant | 24 ga (0.70 mm), low pressure (500 Pa) class, Seal class A | m² | 10.32 | 10 |  | GF
B.7 | Galvanised sheet steel rectangular duct incl. fittings, joints, sealant | 26 ga (0.55 mm), low pressure (500 Pa) class, Seal class A | m² | 18.07 | 10 |  | GF
B.8 | Galvanised sheet steel round spiral duct incl. fittings, joints, sealant | 26 ga (0.55 mm), low pressure (500 Pa) class, Seal class A | m² | 11.52 | 10 |  | GF
C. FLEXIBLE DUCT
C.1 | Insulated flexible duct Ø200 | Insulated flexible duct, aluminium core, 25 mm insulation, UL 181 Class 1 | m | 2.38 | 10 |  | FF
C.2 | Insulated flexible duct Ø300 | Insulated flexible duct, aluminium core, 25 mm insulation, UL 181 Class 1 | m | 2.88 | 10 |  | FF
C.3 | Insulated flexible duct Ø150 | Insulated flexible duct, aluminium core, 25 mm insulation, UL 181 Class 1 | m | 2.44 | 10 |  | GF
C.4 | Insulated flexible duct Ø250 | Insulated flexible duct, aluminium core, 25 mm insulation, UL 181 Class 1 | m | 2.38 | 10 |  | GF
C.5 | Insulated flexible duct Ø350 | Insulated flexible duct, aluminium core, 25 mm insulation, UL 181 Class 1 | m | 2.88 | 10 |  | GF
D. AIR TERMINALS AND LOUVERS
D.1 | 4-way square ceiling diffuser with OBD and plenum box | SD-150 neck Ø150, face 300x300 | No. | 6 | 0 |  | FF | Tags: SD-FF-03, SD-FF-07, SD-FF-08, SD-FF-09, SD-FF-10, SD-FF-11
D.2 | 4-way square ceiling diffuser with OBD and plenum box | SD-150 neck Ø150, face 300x300 | No. | 4 | 0 |  | GF | Tags: SD-GF-05, SD-GF-06, SD-GF-07, SD-GF-08
D.3 | 4-way square ceiling diffuser with OBD and plenum box | SD-200 neck Ø200, face 450x450 | No. | 3 | 0 |  | FF | Tags: SD-FF-04, SD-FF-05, SD-FF-06
D.4 | 4-way square ceiling diffuser with OBD and plenum box | SD-200 neck Ø200, face 450x450 | No. | 2 | 0 |  | GF | Tags: SD-GF-03, SD-GF-04
D.5 | 4-way square ceiling diffuser with OBD and plenum box | SD-250 neck Ø250, face 600x600 | No. | 3 | 0 |  | FF | Tags: SD-FF-01, SD-FF-02, SD-FF-12
D.6 | 4-way square ceiling diffuser with OBD and plenum box | SD-250 neck Ø250, face 600x600 | No. | 4 | 0 |  | GF | Tags: SD-GF-01, SD-GF-02, SD-GF-09, SD-GF-10
D.7 | Door transfer grille | 450x150 aluminium sight-proof, by door supplier / HVAC | No. | 5 | 0 |  | FF | rooms FF-03, FF-10, FF-08, FF-05, FF-09
D.8 | Door transfer grille | 450x150 aluminium sight-proof, by door supplier / HVAC | No. | 3 | 0 |  | GF | rooms GF-01, GF-05, GF-03
D.9 | Exhaust grille | 150x150, aluminium, eggcrate | No. | 4 | 0 |  | FF | Tags: EG-FF-01, EG-FF-02, EG-FF-03, EG-FF-04
D.10 | Exhaust grille | 150x150, aluminium, eggcrate | No. | 3 | 0 |  | GF | Tags: EG-GF-02, EG-GF-03, EG-GF-04
D.11 | Exhaust grille | 200x200, aluminium, eggcrate | No. | 1 | 0 |  | GF | Tags: EG-GF-01
D.12 | Exhaust wall louver / cowl with backdraft shutter | 200x200, aluminium | No. | 4 | 0 |  | FF | Tags: EAL-FF-01, EAL-FF-02, EAL-FF-03, EAL-FF-04
D.13 | Exhaust wall louver / cowl with backdraft shutter | 200x200, aluminium | No. | 3 | 0 |  | GF | Tags: EAL-GF-02, EAL-GF-03, EAL-GF-04
D.14 | Exhaust wall louver / cowl with backdraft shutter | 300x200, aluminium | No. | 1 | 0 |  | GF | Tags: EAL-GF-01
D.15 | Fresh air louver with bird screen and sand trap | 200x200, aluminium | No. | 1 | 0 |  | FF | Tags: FAL-FF-01
D.16 | Fresh air louver with bird screen and sand trap | 300x200, aluminium | No. | 1 | 0 |  | GF | Tags: FAL-GF-01
D.17 | Fresh air louver with bird screen and sand trap | 450x300, aluminium | No. | 1 | 0 |  | FF | Tags: FAL-FF-02
D.18 | Fresh air louver with bird screen and sand trap | 450x300, aluminium | No. | 1 | 0 |  | GF | Tags: FAL-GF-02
D.19 | Return grille with filter and plenum box | 600x450, aluminium, eggcrate | No. | 1 | 0 |  | FF | Tags: RG-FF-01
D.20 | Return grille with filter and plenum box | 600x450, aluminium, eggcrate | No. | 1 | 0 |  | GF | Tags: RG-GF-01
D.21 | Return grille with filter and plenum box | 900x600, aluminium, eggcrate | No. | 1 | 0 |  | FF | Tags: RG-FF-02
D.22 | Return grille with filter and plenum box | 900x600, aluminium, eggcrate | No. | 1 | 0 |  | GF | Tags: RG-GF-02
E. DAMPERS
E.1 | Volume control damper (branch), opposed blade | 150x150 | No. | 3 | 0 |  | FF | zones Z-FF-02
E.2 | Volume control damper (branch), opposed blade | 200x200 | No. | 1 | 0 |  | FF | zones Z-FF-02
E.3 | Volume control damper (branch), opposed blade | 300x300 | No. | 1 | 0 |  | FF | zones Z-FF-01
E.4 | Volume control damper (branch), opposed blade | 400x300 | No. | 1 | 0 |  | FF | zones Z-FF-02
E.5 | Volume control damper (branch), opposed blade | 200x150 | No. | 1 | 0 |  | GF | zones Z-GF-04
E.6 | Volume control damper (branch), opposed blade | 300x300 | No. | 1 | 0 |  | GF | zones Z-GF-04
E.7 | Volume control damper (branch), opposed blade | 400x300 | No. | 1 | 0 |  | GF | zones Z-GF-04
E.8 | Volume control damper on fresh air duct | Ø150 | No. | 1 | 0 |  | Z-GF-03
E.9 | Motorised fresh air damper, 24 V on/off, interlocked with indoor unit | Ø150 | No. | 1 | 0 |  | Z-GF-03
E.10 | Volume control damper on fresh air duct | Ø200 | No. | 1 | 0 |  | Z-GF-04
E.11 | Motorised fresh air damper, 24 V on/off, interlocked with indoor unit | Ø200 | No. | 1 | 0 |  | Z-GF-04
E.12 | Volume control damper on fresh air duct | Ø125 | No. | 1 | 0 |  | Z-FF-01
E.13 | Motorised fresh air damper, 24 V on/off, interlocked with indoor unit | Ø125 | No. | 1 | 0 |  | Z-FF-01
E.14 | Volume control damper on fresh air duct | Ø200 | No. | 1 | 0 |  | Z-FF-02
E.15 | Motorised fresh air damper, 24 V on/off, interlocked with indoor unit | Ø200 | No. | 1 | 0 |  | Z-FF-02
E.16 | Backdraft (non-return) damper at exhaust discharge | Gravity type | No. | 8 | 0 |  | All
E.17 | Fire dampers at fire-rated walls / floors | UL 555, 1.5 h, fusible link | No. | 0 | 0 |  | TBC | Fire dampers where ducts cross fire-rated walls/floors - fire compartmentation not shown on architectural plan: confirm with fire consultant.
F. FANS
F.1 | Exhaust fan, ceiling | EF-25: 25 L/s @ 60 Pa, 15 W | No. | 4 | 0 |  | FF | Tags: EF-FF-01, EF-FF-02, EF-FF-03, EF-FF-04
F.2 | Exhaust fan, ceiling | EF-25: 25 L/s @ 60 Pa, 15 W | No. | 3 | 0 |  | GF | Tags: EF-GF-02, EF-GF-03, EF-GF-04
F.3 | Exhaust fan, ceiling | EF-50: 50 L/s @ 80 Pa, 25 W | No. | 1 | 0 |  | GF | Tags: EF-GF-01
G. REFRIGERANT / CHILLED WATER PIPING AND FITTINGS
G.1 | Copper refrigerant pipe, ACR grade, seamless, deoxidised | OD 6.35 mm (1/4") | m | 63.5 | 10 |  | All | riser + floor + roof runs
G.2 | Copper refrigerant pipe, ACR grade, seamless, deoxidised | OD 9.52 mm (3/8") | m | 97.5 | 10 |  | All | riser + floor + roof runs
G.3 | Copper refrigerant pipe, ACR grade, seamless, deoxidised | OD 12.7 mm (1/2") | m | 47 | 10 |  | All | riser + floor + roof runs
G.4 | Copper refrigerant pipe, ACR grade, seamless, deoxidised | OD 15.88 mm (5/8") | m | 81 | 10 |  | All | riser + floor + roof runs
G.5 | Copper refrigerant fittings (long-radius elbows / couplings), brazed with nitrogen purge | OD 6.35 mm | No. | 24 | 10 |  | All
G.6 | Copper refrigerant fittings (long-radius elbows / couplings), brazed with nitrogen purge | OD 9.52 mm | No. | 32 | 10 |  | All
G.7 | Copper refrigerant fittings (long-radius elbows / couplings), brazed with nitrogen purge | OD 12.7 mm | No. | 16 | 10 |  | All
G.8 | Copper refrigerant fittings (long-radius elbows / couplings), brazed with nitrogen purge | OD 15.88 mm | No. | 24 | 10 |  | All
H. THERMAL INSULATION
H.1 | Duct insulation (supply / return / fresh air) | 25 mm glass wool 24 kg/m3 with FSK facing (external wrap) | m² | 39 | 10 |  | FF
H.2 | Duct insulation (supply / return / fresh air) | 25 mm glass wool 24 kg/m3 with FSK facing (hot outdoor air) | m² | 5.29 | 10 |  | FF
H.3 | Duct insulation (supply / return / fresh air) | 25 mm glass wool 24 kg/m3 with FSK facing (external wrap) | m² | 34.11 | 10 |  | GF
H.4 | Duct insulation (supply / return / fresh air) | 25 mm glass wool 24 kg/m3 with FSK facing (hot outdoor air) | m² | 4.95 | 10 |  | GF
H.5 | Closed-cell elastomeric pipe insulation, UV-protected outdoors | for OD 6.35 mm, 13 mm thick | m | 63.5 | 10 |  | All
H.6 | Closed-cell elastomeric pipe insulation, UV-protected outdoors | for OD 9.52 mm, 19 mm thick | m | 97.5 | 10 |  | All
H.7 | Closed-cell elastomeric pipe insulation, UV-protected outdoors | for OD 12.7 mm, 19 mm thick | m | 47 | 10 |  | All
H.8 | Closed-cell elastomeric pipe insulation, UV-protected outdoors | for OD 15.88 mm, 19 mm thick | m | 81 | 10 |  | All
I. CONDENSATE DRAIN
I.1 | uPVC condensate pipe incl. fittings, slope 1 % | Ø25, uPVC Class E / Sch.40, insulated 9 mm where run in ceiling void | m | 8.91 | 10 |  | FF | Tags: CD-IU-FF-01, CD-IU-FF-02
I.2 | Condensate trap / P-trap with cleanout at unit | Ø25 | No. | 2 | 10 |  | FF
I.3 | uPVC condensate pipe incl. fittings, slope 1 % | Ø25, uPVC Class E / Sch.40, insulated 9 mm where run in ceiling void | m | 21.03 | 10 |  | GF | Tags: CD-IU-GF-01, CD-IU-GF-02, CD-IU-GF-03, CD-IU-GF-04
I.4 | Condensate trap / P-trap with cleanout at unit | Ø25 | No. | 4 | 10 |  | GF
J. SUPPORTS AND HANGERS
J.1 | Duct hangers: threaded rod + angle/strap, galvanised | @ 2.4 m max (pairs) | No. | 23 | 5 |  | FF
J.2 | Duct hangers: threaded rod + angle/strap, galvanised | @ 2.4 m max (pairs) | No. | 19 | 5 |  | GF
J.3 | Refrigerant pipe supports / clamps with insulation saddles | @ 1.2 m | No. | 121 | 5 |  | All
J.4 | Condensate pipe clips | @ 1.0 m | No. | 30 | 5 |  | All
J.5 | Outdoor unit steel support frame / concrete plinth with anti-vibration pads | Galvanised, by structural check | No. | 6 | 5 |  | Roof
K. CONTROLS
K.1 | Wired room controller | wired controller | No. | 1 | 0 |  | Z-GF-01 | Tags: T-GF-01
K.2 | Wired room controller | wired controller | No. | 1 | 0 |  | Z-GF-02 | Tags: T-GF-02
K.3 | Wired programmable thermostat / controller | wired programmable thermostat | No. | 1 | 0 |  | Z-GF-03 | Tags: T-GF-03
K.4 | Wired programmable thermostat / controller | wired programmable thermostat | No. | 1 | 0 |  | Z-GF-04 | Tags: T-GF-04
K.5 | Wired programmable thermostat / controller | wired programmable thermostat | No. | 1 | 0 |  | Z-FF-01 | Tags: T-FF-01
K.6 | Wired programmable thermostat / controller | wired programmable thermostat | No. | 1 | 0 |  | Z-FF-02 | Tags: T-FF-02
K.7 | Control wiring, interlocks (FA damper / FA fan to unit), communication cable | Shielded 2-core, in conduit | Lot | 1 | 0 |  | All | 4 motorised damper interlocks
L. TESTING AND COMMISSIONING
L.1 | Pressure testing of refrigerant piping (nitrogen, 24 h hold) and evacuation |  | Lot | 1 | 0 |  | All
L.2 | Ductwork leakage testing per SMACNA HVAC Air Duct Leakage Test Manual / DW/143 (sample basis) |  | Lot | 1 | 0 |  | All
L.3 | Testing, adjusting and balancing (TAB) of all air systems by NEBB/AABC certified agency |  | Lot | 1 | 0 |  | All
L.4 | Commissioning of indoor/outdoor units, fans and controls incl. functional performance tests |  | Lot | 1 | 0 |  | All
L.5 | As-built drawings, O&M manuals and training |  | Lot | 1 | 0 |  | All

## Notes
PRELIMINARY DESIGN - FOR COORDINATION ONLY. To be checked and stamped by a qualified HVAC engineer before construction.
Quantities are measured from the preliminary design model (design.json) and include the waste/allowance % shown (editable, yellow cells).
Ductwork measured as external surface area of straight duct by gauge; fittings covered by the allowance.
Equipment and terminals are generic sizes - replace with the approved brand's model numbers.
Fire dampers, builder's work openings, electrical power wiring and BMS integration are excluded / TBC.
See assumptions.md and the design calculation report for the design basis.