HVAC DESIGN CALCULATION REPORT

Sample Villa - Riyadh

Riyadh, Saudi Arabia

Building type: villa - 2 floor(s)

Code basis: Saudi Building Code + ASHRAE   |   Units: SI

Issue: P0 (preliminary)   2026-10-15

PRELIMINARY DESIGN - FOR COORDINATION ONLY. To be checked and stamped by a qualified HVAC engineer before construction.

# 1. Design basis

## 1.1 Codes and standards

| Ref | Code / standard |
| --- | --- |
| SBC501 | SBC 501 Saudi Mechanical Code (2018, as amended) |
| SBC601 | SBC 601 Saudi Energy Conservation Code - Commercial |
| SBC602 | SBC 602 Saudi Energy Conservation Code - Residential |
| A62.1 | ANSI/ASHRAE Standard 62.1-2019 Ventilation for Acceptable IAQ |
| A90.1 | ANSI/ASHRAE/IES Standard 90.1-2019 Energy Standard |
| AF | ASHRAE Handbook - Fundamentals (CLTD/SCL/CLF method 1997 Ch.28; climate data 2021 Ch.14) |
| SMACNA | SMACNA HVAC Duct Construction Standards - Metal and Flexible, 3rd ed. 2005 |

## 1.2 Design conditions

| Parameter | Value | Basis |
| --- | --- | --- |
| Outdoor summer design (0.4 %) | 45.6 °C DB / 19.4 °C MCWB, W = 4.4 g/kg | ASHRAE 2021 Ch.14 (0.4% cool / 99.6% heat) - OERK |
| Daily range | 14.6 K | ASHRAE 2021 Ch.14 (0.4% cool / 99.6% heat) - OERK |
| Outdoor winter design (99.6 %) | 6.6 °C | ASHRAE 2021 Ch.14 (0.4% cool / 99.6% heat) - OERK |
| Indoor cooling | 24.0 °C, 50 % RH (W = 10.0 g/kg) | SBC 602 §302 / SBC 601 §302.1 (design conditions); ASHRAE Fundamentals 2021 Ch.14 (0.4 % cooling, 99.6 % heating) |
| Indoor heating | 21.0 °C | SBC 602 §302 / SBC 601 §302.1 (design conditions); ASHRAE Fundamentals 2021 Ch.14 (0.4 % cooling, 99.6 % heating) |
| Site elevation / pressure | 612 m / 94.19 kPa; air factors 1.143 W/(L/s·K), 2798 W/(L/s·kg/kg) | ASHRAE Fundamentals Ch.1 |
| Latitude / design month | 24.71° / July (CLTD tables) | ASHRAE Fundamentals 1997 Ch.28 CLTD/SCL/CLF method, Tables 30-36 |

Code reference: SBC 602 §302 / SBC 601 §302.1 (design conditions); ASHRAE Fundamentals 2021 Ch.14 (0.4 % cooling, 99.6 % heating)

## 1.3 Building envelope

| Element | U-value / property | Basis |
| --- | --- | --- |
| External wall | 0.40 W/m²K (CLTD wall group D) | SBC602 |
| Roof | 0.20 W/m²K (roof_insulated_concrete) | SBC602 |
| Glazing | 2.67 W/m²K, SHGC 0.25 (SC 0.29) | SBC602 |
| Slab edge (heating) | F = 1.2 W/m·K | SBC602 |

Code reference: SBC 602 Ch.4 prescriptive envelope table / SBC 601 Ch.5 (max U-factor, SHGC)

## 1.4 Internal loads

| Space type | Occupancy | Activity | Lighting W/m² | Equipment W/m² + fixed | OA category | Exhaust | Cooled |
| --- | --- | --- | --- | --- | --- | --- | --- |
| bath | 0 persons | seated | 8 | 0 + 0 W |  | toilet_private | no |
| bedroom | 2 persons | sleeping | 8 | 5 + 0 W | dwelling |  | yes |
| corridor | 0 persons | seated | 6 | 0 + 0 W | corridor |  | yes |
| dining | 2.5 m²/person | seated | 10 | 3 + 0 W | dwelling |  | yes |
| dressing | 0 persons | seated | 8 | 0 + 0 W | dwelling |  | yes |
| hall | 1 persons | seated | 8 | 0 + 0 W | corridor |  | yes |
| kitchen | 2 persons | light_work | 10 | 0 + 1500 W | dwelling | kitchen_residential | yes |
| laundry | 0 persons | light_work | 8 | 0 + 0 W |  | laundry | no |
| living | 4.0 m²/person | seated | 10 | 8 + 0 W | dwelling |  | yes |
| maid_room | 1 persons | sleeping | 8 | 5 + 0 W | dwelling |  | yes |
| majlis | 2.5 m²/person | seated | 12 | 4 + 0 W | dwelling |  | yes |
| master_bedroom | 2 persons | sleeping | 8 | 6 + 0 W | dwelling |  | yes |
| shaft | 0 persons | seated | 0 | 0 + 0 W |  |  | no |
| stair | 0 persons | seated | 6 | 0 + 0 W | corridor |  | yes |
| store | 0 persons | seated | 5 | 0 + 0 W |  |  | no |

Code reference: ASHRAE Fundamentals 2021 Ch.18 Table 1 (people), Tables 2-3 (lighting), Tables 5-9 (equipment)

## 1.5 Assumptions

All assumptions are logged in assumptions.md. Items marked 'confirm' must be confirmed by the engineer of record.

| ID | Step | Assumption | Source | Status |
| --- | --- | --- | --- | --- |
| A001 | A-read | Page 1 scale 1:100 (title+dimensions, confidence high) | scale_detect.py | default |
| A002 | A-read | Page 1 north = 19.6 deg clockwise from page-up (detected from north arrow) | pdf_reader.py | default |
| A003 | A-read | Page 2 scale 1:100 (title+dimensions, confidence high) | scale_detect.py | default |
| A004 | A-read | Page 2 north = 19.6 deg clockwise from page-up (detected from north arrow) | pdf_reader.py | default |
| A005 | A-read | Page 3 scale 1:100 (title+dimensions, confidence high) | scale_detect.py | default |
| A006 | A-read | Page 3 north = 19.6 deg clockwise from page-up (detected from north arrow) | pdf_reader.py | default |
| A007 | B-loads | Outdoor design 45.6 °C DB / 19.4 °C MCWB (0.4 %), daily range 14.6 K, heating 6.6 °C (99.6 %), elevation 612.0 m (ASHRAE 2021 Ch.14 (0.4% cool / 99.6% heat) - OERK, approximate - verify) | references/climate_data.csv | default |
| A008 | B-loads | Indoor design 24.0 °C / 50 % RH cooling, 21.0 °C heating | SBC 602 §302 / SBC 601 §302.1 (design conditions); ASHRAE Fundamentals 2021 Ch.14 (0.4 % cooling, 99.6 % heating) | default |
| A009 | B-loads | Envelope U-values = code maximum (SBC602: wall 0.4, roof 0.2, glazing U 2.67 / SHGC 0.25 W/m²K) - actual build-up not given | SBC 602 Ch.4 prescriptive envelope table / SBC 601 Ch.5 (max U-factor, SHGC) | CONFIRM |
| A010 | B-loads | Cooling loads by CLTD/SCL/CLF; CLTD tables for wall group D, roof 'roof_insulated_concrete', latitude row nearest 24.71°, July; colour factor K=0.83 (medium walls), roof K=1.0; glass with interior shading=True | ASHRAE Fundamentals 1997 Ch.28 CLTD/SCL/CLF method, Tables 30-36 | CONFIRM |
| A011 | B-loads | CLTD/LM/SHGF/CLF tables in references/cltd_tables.json are transcribed-approximate - verify against licensed ASHRAE 1997 Ch.28 tables | references/cltd_tables.json | CONFIRM |
| A012 | B-loads | CLF for people/lights/equipment = 1.0 (24 h operation, no storage credit) | ASHRAE Fundamentals 1997 Ch.28 CLTD/SCL/CLF method, Tables 30-36 | default |
| A013 | B-loads | Partitions/floors between conditioned and exhaust-only rooms (baths, stores) not counted: those rooms are near room temperature | designer judgement | default |
| A014 | B-loads | Outdoor humidity ratio 4.4 g/kg < indoor 10.0 g/kg at design: outdoor-air latent load taken as 0 (conservative); check a dehumidification design day | ASHRAE Fundamentals 2021 Ch.14 (DP design) | CONFIRM |
| A015 | B-loads | Supply air 13.0 °C (room-supply ΔT 11.0 K) for airflow | designer default | default |
| A016 | B-loads | Infiltration by air-change method: {'one_exterior_side': 0.5, 'two_plus_exterior_sides': 0.75, 'no_exterior': 0.0} ACH (residential) | ASHRAE Fundamentals 2021 Ch.16 §'Residential air change method' | default |
| A017 | B-loads | Occupancy, lighting and equipment densities from references/space_types.json | ASHRAE Fundamentals 2021 Ch.18 Table 1 (people), Tables 2-3 (lighting), Tables 5-9 (equipment) | default |
| A018 | B-zoning | Zoning: own zone for ['majlis', 'master_bedroom']; other ducted rooms grouped by position per floor up to 17.6 kW per unit (incl. safety factor) | references/design_defaults.json zoning | CONFIRM |
| A019 | B-zoning | Rooms exhaust-only (not cooled; make-up by transfer air): GF-09, GF-11, GF-13, FF-01, FF-02, FF-12, FF-14 | references/space_types.json | CONFIRM |
| A020 | B-vent | Z-GF-01 (KITCHEN) has no exterior wall: its 14 L/s OA is supplied via Z-GF-04 and transferred | SBC 501 §403.3.1.1 & Table 403.3.1.1; ASHRAE 62.1-2019 §6.2.2.1 Eq.6-1, Table 6-1 | CONFIRM |
| A021 | B-vent | Zone air distribution effectiveness Ez = 0.8 (heat-pump heating with ceiling supply of warm air) | ASHRAE 62.1-2019 §6.2.2.2 Table 6-2 (Ez) | default |
| A022 | B-vent | Exhaust fans sized for the intermittent (rated) rate; continuous operation would allow the lower rate | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) | default |
| A023 | B-equip | Safety factor 10% on cooling and 10% on heating, applied to coil loads at selection (shown in tables) | Designer allowance - not a code requirement | CONFIRM |
| A024 | B-equip | Nominal (T1) capacities derated x0.88 for 45.6 °C outdoor design (T3) - replace with brand T3 data | references/equipment_catalog.json t3_derate | CONFIRM |
| A025 | B-equip | Equipment from GENERIC catalogue (references/equipment_catalog.json) - replace with the approved brand | references/equipment_catalog.json | CONFIRM |
| A026 | B-equip | Minimum supply per served room 30 L/s (smallest diffuser) | references/air_terminals.json | default |
| A027 | B-equip | GF-06 KITCHEN has no exterior wall: wall split on interior wall, refrigerant/condensate run in ceiling | designer judgement | CONFIRM |
| A028 | B-equip | IU-GF-02 (WS-09) is 141 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A029 | B-equip | Z-GF-03 indoor unit in the ceiling void of GF-02 ENTRANCE HALL (service space next to the zone) | references/design_defaults.json unit_host_preference | CONFIRM |
| A030 | B-equip | Z-GF-04: sensible capacity governs (8.2 kW sensible at catalogue SHR) - DS-48 chosen instead of DS-36; brand data at actual (dry) entering conditions may allow the smaller unit | designer note | CONFIRM |
| A031 | B-equip | Z-GF-04 indoor unit in the ceiling void of GF-04 CORRIDOR (service space next to the zone) | references/design_defaults.json unit_host_preference | CONFIRM |
| A032 | B-equip | IU-FF-01 (DS-24) is 127 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A033 | B-equip | Z-FF-01 indoor unit in the ceiling void of FF-04 DRESSING (service space next to the zone) | references/design_defaults.json unit_host_preference | CONFIRM |
| A034 | B-equip | Z-FF-02 indoor unit in the ceiling void of FF-07 LOBBY (service space next to the zone) | references/design_defaults.json unit_host_preference | CONFIRM |
| A035 | B-equip | Outdoor units grouped on the roof near the riser/shaft with 0.6 m service clearance; check structure, parapet height and acoustic screening | designer judgement | CONFIRM |
| A036 | B-ducts | Ducts sized by equal friction 0.8 Pa/m with velocity limits {'main': 5.0, 'branch': 3.5, 'runout': 2.5, 'return': 3.5, 'fresh_air': 4.0, 'exhaust': 4.0} m/s; max duct depth 300 mm from ceiling void | ASHRAE Fundamentals 2021 Ch.21 (equal friction method, Eq.18-19 Altshul-Tsal) | default |
| A037 | B-ducts | Fittings allowed as +50% equivalent length; unit plenum/filter 40.0 Pa | designer default | CONFIRM |
| A038 | B-ducts | Duct routes are schematic trunk-and-branch lines over the plan; coordinate with structure (beams), lighting and other services | designer judgement | CONFIRM |
| A039 | B-ducts | Return air from rooms via door undercut / door transfer grilles to the return grille near the unit | ASHRAE Fundamentals 2021 Ch.21 (equal friction method, Eq.18-19 Altshul-Tsal) | CONFIRM |
| A040 | B-pipes | Refrigerant pipe sizes from GENERIC table (references/pipe_sizing.json) - replace with the selected brand's table | SBC 501 Ch.11 §1107 (refrigerant piping); ASHRAE 15; manufacturer piping tables | CONFIRM |
| A041 | B-pipes | Refrigerant length = route x (1+10%) + vertical rise to roof (+1.5 m allowance) | designer default | default |
| A042 | B-pipes | Condensate to nearest wet-room floor drain / stack with trap; min 25 mm, slope 1.0 % | SBC 501 §307.2.1 (disposal), §307.2.2 Table 307.2.2 (drain size), slope >= 1 % | CONFIRM |

# 2. Room schedule (Gate 1 approved)

| ID | Room | Type | Area m² | Ceiling m | Exterior walls (orient. m) | Windows | Roof exp. | Cooled |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| GF-01 | MAJLIS | majlis | 27.79 | 3.0 | N 5.7, W 4.68 | W1 N 1.8x1.5, W2 W 1.2x1.5 | 0% | yes |
| GF-02 | ENTRANCE HALL | hall | 16.55 | 3.0 | N 3.41 | - | 0% | yes |
| GF-03 | LIVING | living | 30.32 | 3.0 | N 6.21, E 4.7 | W4 N 2.4x2.1, W1 E 1.8x1.5 | 0% | yes |
| GF-04 | CORRIDOR | corridor | 7.16 | 3.0 | - | - | 0% | yes |
| GF-05 | DINING | dining | 21.31 | 3.0 | W 4.35 | W1 W 1.8x1.5 | 0% | yes |
| GF-06 | KITCHEN | kitchen | 21.92 | 3.0 | - | - | 0% | yes |
| GF-07 | MAID ROOM | maid_room | 12.99 | 3.0 | E 3.84 | W2 E 1.2x1.5 | 0% | yes |
| GF-08 | STAIR | stair | 12.54 | 3.0 | S 2.91 | - | 0% | yes |
| GF-09 | MAID WC | bath | 6.73 | 3.0 | S 2.34 | W3 S 0.6x0.6 | 0% | no |
| GF-10 | SHAFT | shaft | 2.11 | 3.0 | E 2.75, S 0.75 | - | 0% | no |
| GF-11 | GUEST WC | bath | 5.19 | 3.0 | S 2.19, W 2.25 | W3 S 0.6x0.6 | 0% | no |
| GF-12 | STORE | store | 5.43 | 3.0 | S 2.38 | - | 0% | no |
| GF-13 | LAUNDRY | laundry | 7.87 | 3.0 | S 4.33 | W2 S 1.2x1.5 | 0% | no |
| FF-01 | MASTER BATH | bath | 8.09 | 3.0 | N 2.85 | W3 N 0.6x0.6 | 100% | no |
| FF-02 | BATH 2 | bath | 6.31 | 3.0 | N 2.25, E 2.69 | W3 E 0.6x0.6 | 100% | no |
| FF-03 | MASTER BEDROOM | master_bedroom | 27.79 | 3.0 | N 5.7, W 4.67 | W1 N 1.8x1.5, W2 W 1.2x1.5 | 100% | yes |
| FF-04 | DRESSING | dressing | 5.73 | 3.0 | - | - | 100% | yes |
| FF-05 | BEDROOM 2 | bedroom | 21.37 | 3.0 | N 4.35 | W1 N 1.8x1.5 | 100% | yes |
| FF-06 | LINEN | store | 4.35 | 3.0 | E 1.91 | - | 100% | no |
| FF-07 | LOBBY | corridor | 7.23 | 3.0 | - | - | 100% | yes |
| FF-08 | BEDROOM 3 | bedroom | 19.76 | 3.0 | - | - | 100% | yes |
| FF-09 | BEDROOM 4 | bedroom | 13.04 | 3.0 | E 3.85 | W1 E 1.8x1.5 | 100% | yes |
| FF-10 | FAMILY LIVING | living | 32.64 | 3.0 | S 4.67, W 6.69 | W4 W 2.4x2.1, W2 S 1.2x1.5 | 100% | yes |
| FF-11 | STAIR | stair | 12.46 | 3.0 | S 2.91 | - | 100% | yes |
| FF-12 | BATH 4 | bath | 6.73 | 3.0 | S 2.34 | W3 S 0.6x0.6 | 100% | no |
| FF-13 | SHAFT | shaft | 2.11 | 3.0 | E 2.75, S 0.75 | - | 100% | no |
| FF-14 | BATH 3 | bath | 10.05 | 3.0 | S 4.33 | W3 S 0.6x0.6 | 100% | no |

# 3. Cooling and heating loads

Method: CLTD/SCL/CLF (ASHRAE Fundamentals 1997 Ch.28). Conduction Q = U·A·CLTDc with CLTDc = (CLTD + LM)·K + (25.5 − Ti) + (Tm − 29.4), Tm = To − DR/2. Glass solar Q = A·SC·SHGF·CLF. People/lights/equipment with CLF = 1.0. Infiltration Qs = Cs·V·ΔT, Ql = Cl·V·ΔW. Loads are computed for solar hours 8-20; each room is sized at its own peak, zones and plant at the coincident (block) peak. Heating: Q = ΣU·A·(Ti − To,w) + infiltration + slab edge, no internal gains.

Code reference: ASHRAE Fundamentals 1997 Ch.28 CLTD/SCL/CLF method, Tables 30-36; ASHRAE Fundamentals 2021 Ch.16 §'Residential air change method'

| ID | Room | m² | Walls | Roof | Glass cond. | Glass solar | People S | Lights | Equip S | Infil S | Sensible W | Latent W | Total W | W/m² | Peak | Supply | Heating W |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| GF-01 | MAJLIS | 27.79 | 273.0 | 0.0 | 205.0 | 370.0 | 840.0 | 333.0 | 111.0 | 368.0 | 2501 | 540 | 3041 | 109.4 | 18:00 | 199 L/s | 828 |
| GF-02 | ENTRANCE HALL | 16.55 | 81.0 | 0.0 | 0.0 | 0.0 | 70.0 | 132.0 | 0.0 | 170.0 | 453 | 45 | 498 | 30.1 | 15:00 | 36 L/s | 243 |
| GF-03 | LIVING | 30.32 | 246.0 | 0.0 | 376.0 | 272.0 | 560.0 | 303.0 | 243.0 | 468.0 | 2468 | 360 | 2828 | 93.3 | 15:00 | 196 L/s | 980 |
| GF-04 | CORRIDOR | 7.16 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 43.0 | 0.0 | 0.0 | 43 | 0 | 43 | 6.0 | 8:00 | 3 L/s | 0 |
| GF-05 | DINING | 21.31 | 123.0 | 0.0 | 123.0 | 418.0 | 630.0 | 213.0 | 64.0 | 188.0 | 1759 | 405 | 2164 | 101.5 | 18:00 | 140 L/s | 400 |
| GF-06 | KITCHEN | 21.92 | 0.0 | 0.0 | 0.0 | 0.0 | 160.0 | 219.0 | 1500.0 | 0.0 | 1879 | 660 | 2539 | 115.8 | 8:00 | 149 L/s | 0 |
| GF-07 | MAID ROOM | 12.99 | 81.0 | 0.0 | 55.0 | 286.0 | 60.0 | 104.0 | 65.0 | 70.0 | 720 | 25 | 745 | 57.4 | 9:00 | 57 L/s | 294 |
| GF-08 | STAIR | 12.54 | 69.0 | 0.0 | 0.0 | 0.0 | 0.0 | 75.0 | 0.0 | 126.0 | 270 | 0 | 270 | 21.6 | 16:00 | 22 L/s | 197 |
| FF-03 | MASTER BEDROOM | 27.79 | 273.0 | 172.0 | 205.0 | 370.0 | 120.0 | 222.0 | 167.0 | 368.0 | 1897 | 50 | 1947 | 70.1 | 18:00 | 151 L/s | 728 |
| FF-04 | DRESSING | 5.73 | 0.0 | 35.0 | 0.0 | 0.0 | 0.0 | 46.0 | 0.0 | 0.0 | 81 | 0 | 81 | 14.2 | 17:00 | 6 L/s | 17 |
| FF-05 | BEDROOM 2 | 21.37 | 85.0 | 123.0 | 131.0 | 83.0 | 120.0 | 171.0 | 107.0 | 220.0 | 1039 | 50 | 1089 | 51.0 | 15:00 | 83 L/s | 387 |
| FF-07 | LOBBY | 7.23 | 0.0 | 45.0 | 0.0 | 0.0 | 0.0 | 43.0 | 0.0 | 0.0 | 88 | 0 | 88 | 12.2 | 17:00 | 7 L/s | 21 |
| FF-08 | BEDROOM 3 | 19.76 | 0.0 | 122.0 | 0.0 | 0.0 | 120.0 | 158.0 | 99.0 | 0.0 | 499 | 50 | 549 | 27.8 | 17:00 | 40 L/s | 57 |
| FF-09 | BEDROOM 4 | 13.04 | 75.0 | 36.0 | 83.0 | 428.0 | 120.0 | 104.0 | 65.0 | 70.0 | 982 | 50 | 1032 | 79.1 | 9:00 | 78 L/s | 295 |
| FF-10 | FAMILY LIVING | 32.64 | 285.0 | 202.0 | 312.0 | 821.0 | 630.0 | 326.0 | 261.0 | 432.0 | 3270 | 405 | 3675 | 112.6 | 18:00 | 260 L/s | 889 |
| FF-11 | STAIR | 12.46 | 69.0 | 76.0 | 0.0 | 0.0 | 0.0 | 75.0 | 0.0 | 126.0 | 345 | 0 | 345 | 27.7 | 16:00 | 27 L/s | 182 |

Conditioned area 290.6 m²; sum of room peaks 20.9 kW; block peak 20.5 kW at 17:00 (70 W/m²); heating 5.5 kW. Safety factors are applied at equipment selection (section 5).

## 3.1 Worked example - FF-10 FAMILY LIVING at 18:00

| Item | Calculation |
| --- | --- |
| Wall S | U 0.4 × A 15.01 m² (gross 16.81) |
| Wall W | U 0.4 × A 19.04 m² (gross 24.08) |
| Window W4 W | cond. U 2.67 × 5.04 m²; solar 5.04 × SC 0.287 × SHGF 690 × CLF |
| Window W2 S | cond. U 2.67 × 1.8 m²; solar 1.8 × SC 0.287 × SHGF 110 × CLF |
| Roof | U 0.2 × 32.64 m² |
| People | 9 persons |
| Infiltration | 0.75 ACH × 97.9 m³ = 20.4 L/s |
| wall | 285.0 W |
| roof | 202.0 W |
| glass_cond | 312.0 W |
| glass_solar | 821.0 W |
| people_s | 630.0 W |
| lights | 326.0 W |
| equip_s | 261.0 W |
| infil_s | 432.0 W |
| people_l | 405 W |
| equip_l | 0 W |
| infil_l | 0 W |
| Room sensible / latent / total | 3270 / 405 / 3675 W |
| Supply airflow | 3270 W / (1.143 × (24.0 − 13.0)) = 260.0 L/s |

# 4. Ventilation and exhaust

Ventilation rate procedure: Vbz = Rp·Pz + Ra·Az; Voz = Vbz / Ez; single-zone Vot = Voz; multiple-zone Vot = (D·ΣRp·Pz + ΣRa·Az)/Ev.

Code reference: SBC 501 §403.3.1.1 & Table 403.3.1.1; ASHRAE 62.1-2019 §6.2.2.1 Eq.6-1, Table 6-1; ASHRAE 62.1-2019 §6.2.2.2 Table 6-2 (Ez); ASHRAE 62.1-2019 §6.2.4.3.1 simplified procedure (Ev)

| Zone | Room | Category | Pz | Az m² | Rp·Pz | Ra·Az | Vbz L/s | Ez | Ev | Zone Vot L/s | OA method |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Z-GF-01 | GF-06 | dwelling | 2 | 21.92 | 5.0 | 6.6 | 11.6 | 0.8 | 1.0 | 14.5 | transfer air from Z-GF-04 (OA added to that zone) |
| Z-GF-02 | GF-07 | dwelling | 1 | 12.99 | 2.5 | 3.9 | 6.4 | 0.8 | 1.0 | 8.0 | through-wall fresh air fan |
| Z-GF-03 | GF-01 | dwelling | 12 | 27.79 | 30.0 | 8.3 | 38.3 | 0.8 | 1.0 | 47.9 | ducted to unit return plenum |
| Z-GF-04 | GF-05 | dwelling | 9 | 21.31 | 22.5 | 6.4 | 28.9 | 0.8 | 0.75 | 106.3 | ducted to unit return plenum |
| Z-GF-04 | GF-08 | corridor | 0 | 12.54 | 0.0 | 3.8 | 3.8 | 0.8 | 0.75 | 106.3 | ducted to unit return plenum |
| Z-GF-04 | GF-04 | corridor | 0 | 7.16 | 0.0 | 2.1 | 2.1 | 0.8 | 0.75 | 106.3 | ducted to unit return plenum |
| Z-GF-04 | GF-02 | corridor | 1 | 16.55 | 0.0 | 5.0 | 5.0 | 0.8 | 0.75 | 106.3 | ducted to unit return plenum |
| Z-GF-04 | GF-03 | dwelling | 8 | 30.32 | 20.0 | 9.1 | 29.1 | 0.8 | 0.75 | 106.3 | ducted to unit return plenum |
| Z-FF-01 | FF-03 | dwelling | 2 | 27.79 | 5.0 | 8.3 | 13.3 | 0.8 | 0.75 | 20.1 | ducted to unit return plenum |
| Z-FF-01 | FF-04 | dwelling | 0 | 5.73 | 0.0 | 1.7 | 1.7 | 0.8 | 0.75 | 20.1 | ducted to unit return plenum |
| Z-FF-02 | FF-10 | dwelling | 9 | 32.64 | 22.5 | 9.8 | 32.3 | 0.8 | 0.75 | 92.6 | ducted to unit return plenum |
| Z-FF-02 | FF-11 | corridor | 0 | 12.46 | 0.0 | 3.7 | 3.7 | 0.8 | 0.75 | 92.6 | ducted to unit return plenum |
| Z-FF-02 | FF-07 | corridor | 0 | 7.23 | 0.0 | 2.2 | 2.2 | 0.8 | 0.75 | 92.6 | ducted to unit return plenum |
| Z-FF-02 | FF-08 | dwelling | 2 | 19.76 | 5.0 | 5.9 | 10.9 | 0.8 | 0.75 | 92.6 | ducted to unit return plenum |
| Z-FF-02 | FF-05 | dwelling | 2 | 21.37 | 5.0 | 6.4 | 11.4 | 0.8 | 0.75 | 92.6 | ducted to unit return plenum |
| Z-FF-02 | FF-09 | dwelling | 2 | 13.04 | 5.0 | 3.9 | 8.9 | 0.8 | 0.75 | 92.6 | ducted to unit return plenum |

| Room | Name | Rule | Exhaust L/s | Mode | Clause |
| --- | --- | --- | --- | --- | --- |
| GF-06 | KITCHEN | kitchen_residential | 50.0 | intermittent | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| GF-09 | MAID WC | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| GF-11 | GUEST WC | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| GF-13 | LAUNDRY | laundry | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| FF-01 | MASTER BATH | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| FF-02 | BATH 2 | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| FF-12 | BATH 4 | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| FF-14 | BATH 3 | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |

Building outdoor air 275 L/s; exhaust 225 L/s (net +50 L/s). ASHRAE 62.2 whole-house cross-check: 65 L/s - design OA exceeds it.

# 5. Zoning and equipment selection

Required capacity = coincident zone load (rooms + outdoor air) × (1 + SF), SF cooling 10%, heating 10%. Nominal capacities × 0.88 for high-ambient (T3) operation. Selection = smallest catalogue unit meeting total, sensible and airflow.

Code reference: Designer allowance - not a code requirement; SASO 2663 / SBC 601 Table C403.3.2 minimum efficiency

| Zone | Rooms | System | Peak h | Rooms kW | OA kW | Block kW | SF | Req. kW | Req. sens kW | Req. air | Selected | Derated kW | Sens kW | Unit air | OA % | Input kW | Heat kW sel/req |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Z-GF-01 | GF-06 | wall_split | 15 | 2.54 | 0.36 | 2.9 | 10% | 3.19 | 2.46 | 149 L/s | IU-GF-01 WS-18 | 4.66 | 3.45 | 250 L/s | 6% | 1.61 | 5.6 / 0.26 |
| Z-GF-02 | GF-07 | wall_split | 15 | 0.67 | 0.2 | 0.86 | 10% | 0.95 | 0.92 | 57 L/s | IU-GF-02 WS-09 | 2.29 | 1.74 | 140 L/s | 6% | 0.76 | 2.9 / 0.47 |
| Z-GF-03 | GF-01 | ducted_split | 16 | 2.98 | 1.16 | 4.14 | 10% | 4.55 | 3.96 | 199 L/s | IU-GF-03 DS-24 | 6.16 | 4.62 | 380 L/s | 13% | 2.19 | 7.6 / 1.78 |
| Z-GF-04 | GF-05, GF-08, GF-04, GF-02, GF-03 | ducted_split | 16 | 5.67 | 2.58 | 8.25 | 10% | 9.07 | 8.18 | 432 L/s | IU-GF-04 DS-48 | 12.32 | 9.12 | 750 L/s | 14% | 4.52 | 15.0 / 3.93 |
| Z-FF-01 | FF-03, FF-04 | ducted_split | 17 | 2.01 | 0.46 | 2.47 | 10% | 2.72 | 2.66 | 181 L/s | IU-FF-01 DS-24 | 6.16 | 4.62 | 380 L/s | 5% | 2.19 | 7.6 / 1.18 |
| Z-FF-02 | FF-10, FF-11, FF-07, FF-08, FF-05, FF-09 | ducted_split | 16 | 6.47 | 2.24 | 8.72 | 10% | 9.59 | 8.98 | 520 L/s | IU-FF-02 DS-48 | 12.32 | 9.12 | 750 L/s | 12% | 4.52 | 15.0 / 3.69 |

| Tag | Model | System | Serves | Nominal | Input kW | Location |
| --- | --- | --- | --- | --- | --- | --- |
| ODU-01 | WS-O-18 | wall_split | IU-GF-01 | 5.3 kW | 1.61 | RF |
| ODU-02 | WS-O-09 | wall_split | IU-GF-02 | 2.6 kW | 0.76 | RF |
| ODU-03 | DS-O-24 | ducted_split | IU-GF-03 | 7.0 kW | 2.19 | RF |
| ODU-04 | DS-O-48 | ducted_split | IU-GF-04 | 14.0 kW | 4.52 | RF |
| ODU-05 | DS-O-24 | ducted_split | IU-FF-01 | 7.0 kW | 2.19 | RF |
| ODU-06 | DS-O-48 | ducted_split | IU-FF-02 | 14.0 kW | 4.52 | RF |

# 6. Duct sizing and air terminals

Equal friction method, target 0.80 Pa/m, velocity limits (m/s) {'main': 5.0, 'branch': 3.5, 'runout': 2.5, 'return': 3.5, 'fresh_air': 4.0, 'exhaust': 4.0}. Darcy-Weisbach with Altshul-Tsal friction factor, roughness 0.09 mm; rectangular sizes from De = 1.30(ab)^0.625/(a+b)^0.25; fittings +50% equivalent length.

Code reference: ASHRAE Fundamentals 2021 Ch.21 (equal friction method, Eq.18-19 Altshul-Tsal); SBC 501 §603.4 metallic ducts; SMACNA 2005 Tables 2-1/2-2 (gauge)

### Z-GF-03 - IU-GF-03 (GF)

| Segment | Type | Serves | Flow | Size | De mm | Velocity | Friction | Length m | Δp | Gauge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D-GF-001 | main | - | 380 L/s | 300x300 | 328 | 4.22 m/s | 0.72 Pa/m | 4.72 | 5.1 Pa | 26 ga (0.55 mm) |
| D-GF-002 | runout | GF-01 | 190 L/s | Ø350 flex | 350 | 1.97 m/s | 0.15 Pa/m | 1.47 | 0.3 Pa | flex |
| D-GF-003 | runout | GF-01 | 190 L/s | Ø350 flex | 350 | 1.97 m/s | 0.15 Pa/m | 1.47 | 0.3 Pa | flex |
| D-GF-004 | main | - | 380 L/s | 400x300 | 378 | 3.17 m/s | 0.36 Pa/m | 1.2 | 0.6 Pa | 24 ga (0.70 mm) |
| D-GF-005 | main | - | 48 L/s | Ø150 round | 150 | 2.71 m/s | 0.76 Pa/m | 2.4 | 2.7 Pa | 26 ga (0.55 mm) |

Critical path: required ESP 71 Pa vs available 75 Pa - OK.

### Z-GF-04 - IU-GF-04 (GF)

| Segment | Type | Serves | Flow | Size | De mm | Velocity | Friction | Length m | Δp | Gauge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D-GF-006 | main | - | 403 L/s | 350x300 | 354 | 3.84 m/s | 0.55 Pa/m | 3.63 | 3.0 Pa | 24 ga (0.70 mm) |
| D-GF-007 | main | - | 340 L/s | 300x300 | 328 | 3.78 m/s | 0.59 Pa/m | 0.1 | 0.1 Pa | 26 ga (0.55 mm) |
| D-GF-008 | main | - | 295 L/s | 300x250 | 299 | 3.93 m/s | 0.71 Pa/m | 1.0 | 1.1 Pa | 26 ga (0.55 mm) |
| D-GF-009 | main | - | 52 L/s | 150x150 | 164 | 2.32 m/s | 0.58 Pa/m | 2.38 | 2.1 Pa | 26 ga (0.55 mm) |
| D-GF-010 | branch | GF-05 | 243 L/s | 300x300 | 328 | 2.70 m/s | 0.32 Pa/m | 3.97 | 1.9 Pa | 26 ga (0.55 mm) |
| D-GF-011 | runout | GF-05 | 121 L/s | Ø250 flex | 250 | 2.47 m/s | 0.34 Pa/m | 1.22 | 0.6 Pa | flex |
| D-GF-012 | runout | GF-05 | 121 L/s | Ø250 flex | 250 | 2.47 m/s | 0.34 Pa/m | 1.22 | 0.6 Pa | flex |
| D-GF-013 | branch | GF-02 | 62 L/s | 200x150 | 189 | 2.08 m/s | 0.40 Pa/m | 1.25 | 0.8 Pa | 26 ga (0.55 mm) |
| D-GF-014 | runout | GF-02 | 31 L/s | Ø150 flex | 150 | 1.77 m/s | 0.35 Pa/m | 1.22 | 0.6 Pa | flex |
| D-GF-015 | runout | GF-02 | 31 L/s | Ø150 flex | 150 | 1.77 m/s | 0.35 Pa/m | 1.22 | 0.6 Pa | flex |
| D-GF-016 | branch | GF-03 | 340 L/s | 400x300 | 378 | 2.84 m/s | 0.30 Pa/m | 6.22 | 2.8 Pa | 24 ga (0.70 mm) |
| D-GF-017 | runout | GF-03 | 170 L/s | Ø300 round | 300 | 2.41 m/s | 0.26 Pa/m | 1.59 | 0.6 Pa | 26 ga (0.55 mm) |
| D-GF-018 | runout | GF-03 | 170 L/s | Ø300 round | 300 | 2.41 m/s | 0.26 Pa/m | 1.59 | 0.6 Pa | 26 ga (0.55 mm) |
| D-GF-019 | main | - | 750 L/s | 850x300 | 534 | 2.94 m/s | 0.23 Pa/m | 1.2 | 0.4 Pa | 22 ga (0.85 mm) |
| D-GF-020 | main | - | 106 L/s | Ø200 round | 200 | 3.38 m/s | 0.80 Pa/m | 6.09 | 7.3 Pa | 26 ga (0.55 mm) |

Critical path: required ESP 72 Pa vs available 100 Pa - OK.

### Z-FF-01 - IU-FF-01 (FF)

| Segment | Type | Serves | Flow | Size | De mm | Velocity | Friction | Length m | Δp | Gauge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D-FF-001 | main | - | 317 L/s | 300x300 | 328 | 3.52 m/s | 0.52 Pa/m | 4.43 | 3.4 Pa | 26 ga (0.55 mm) |
| D-FF-002 | branch | FF-03 | 317 L/s | 350x300 | 354 | 3.02 m/s | 0.36 Pa/m | 1.43 | 0.8 Pa | 24 ga (0.70 mm) |
| D-FF-003 | runout | FF-03 | 158 L/s | Ø300 flex | 300 | 2.24 m/s | 0.23 Pa/m | 1.47 | 0.5 Pa | flex |
| D-FF-004 | runout | FF-03 | 158 L/s | Ø300 flex | 300 | 2.24 m/s | 0.23 Pa/m | 1.47 | 0.5 Pa | flex |
| D-FF-005 | main | - | 380 L/s | 400x300 | 378 | 3.17 m/s | 0.36 Pa/m | 1.2 | 0.6 Pa | 24 ga (0.70 mm) |
| D-FF-006 | main | - | 20 L/s | Ø125 round | 125 | 1.64 m/s | 0.39 Pa/m | 3.89 | 2.3 Pa | 26 ga (0.55 mm) |

Critical path: required ESP 70 Pa vs available 75 Pa - OK.

### Z-FF-02 - IU-FF-02 (FF)

| Segment | Type | Serves | Flow | Size | De mm | Velocity | Friction | Length m | Δp | Gauge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D-FF-007 | riser | - | 750 L/s | 600x300 | 457 | 4.17 m/s | 0.49 Pa/m | 0.76 | 0.6 Pa | 24 ga (0.70 mm) |
| D-FF-008 | main | - | 375 L/s | 300x300 | 328 | 4.16 m/s | 0.70 Pa/m | 4.34 | 4.6 Pa | 26 ga (0.55 mm) |
| D-FF-009 | main | - | 289 L/s | 300x250 | 299 | 3.85 m/s | 0.69 Pa/m | 3.75 | 3.9 Pa | 26 ga (0.55 mm) |
| D-FF-010 | main | - | 232 L/s | 250x250 | 273 | 3.71 m/s | 0.71 Pa/m | 1.05 | 1.1 Pa | 26 ga (0.55 mm) |
| D-FF-011 | main | - | 113 L/s | 200x200 | 219 | 2.81 m/s | 0.57 Pa/m | 2.92 | 2.5 Pa | 26 ga (0.55 mm) |
| D-FF-012 | branch | FF-10 | 375 L/s | 400x300 | 378 | 3.12 m/s | 0.35 Pa/m | 0.9 | 0.5 Pa | 24 ga (0.70 mm) |
| D-FF-013 | runout | FF-10 | 125 L/s | Ø300 round | 300 | 1.77 m/s | 0.15 Pa/m | 1.97 | 0.4 Pa | 26 ga (0.55 mm) |
| D-FF-014 | runout | FF-10 | 125 L/s | Ø300 round | 300 | 1.77 m/s | 0.15 Pa/m | 2.8 | 0.6 Pa | 26 ga (0.55 mm) |
| D-FF-015 | runout | FF-10 | 125 L/s | Ø300 round | 300 | 1.77 m/s | 0.15 Pa/m | 3.12 | 0.7 Pa | 26 ga (0.55 mm) |
| D-FF-016 | branch | FF-11 | 43 L/s | 150x150 | 164 | 1.92 m/s | 0.41 Pa/m | 2.68 | 1.7 Pa | 26 ga (0.55 mm) |
| D-FF-017 | branch | FF-07 | 43 L/s | 150x150 | 164 | 1.92 m/s | 0.41 Pa/m | 0.75 | 0.5 Pa | 26 ga (0.55 mm) |
| D-FF-018 | branch | FF-08 | 57 L/s | 150x150 | 164 | 2.54 m/s | 0.68 Pa/m | 0.25 | 0.3 Pa | 26 ga (0.55 mm) |
| D-FF-019 | branch | FF-05 | 119 L/s | 200x200 | 219 | 2.97 m/s | 0.63 Pa/m | 4.47 | 4.2 Pa | 26 ga (0.55 mm) |
| D-FF-020 | runout | FF-05 | 60 L/s | Ø200 flex | 200 | 1.89 m/s | 0.28 Pa/m | 1.22 | 0.5 Pa | flex |
| D-FF-021 | runout | FF-05 | 60 L/s | Ø200 flex | 200 | 1.89 m/s | 0.28 Pa/m | 1.22 | 0.5 Pa | flex |
| D-FF-022 | main | - | 750 L/s | 850x300 | 534 | 2.94 m/s | 0.23 Pa/m | 1.2 | 0.4 Pa | 22 ga (0.85 mm) |
| D-FF-023 | main | - | 93 L/s | Ø200 round | 200 | 2.95 m/s | 0.62 Pa/m | 6.12 | 5.7 Pa | 26 ga (0.55 mm) |

Critical path: required ESP 73 Pa vs available 100 Pa - OK.

## 6.1 Supply diffuser schedule

| Tag | Room | Model | Flow | NC | Throw m |
| --- | --- | --- | --- | --- | --- |
| SD-GF-01 | GF-01 | SD-250 | 190 L/s | 28 | 2.9 |
| SD-GF-02 | GF-01 | SD-250 | 190 L/s | 28 | 2.9 |
| SD-GF-03 | GF-05 | SD-200 | 121 L/s | 26 | 2.2 |
| SD-GF-04 | GF-05 | SD-200 | 121 L/s | 26 | 2.2 |
| SD-GF-05 | GF-08 | SD-150 | 52 L/s | 18 | 1.3 |
| SD-GF-06 | GF-04 | SD-150 | 52 L/s | 18 | 1.3 |
| SD-GF-07 | GF-02 | SD-150 | 31 L/s | 11 | 0.8 |
| SD-GF-08 | GF-02 | SD-150 | 31 L/s | 11 | 0.8 |
| SD-GF-09 | GF-03 | SD-250 | 170 L/s | 26 | 2.6 |
| SD-GF-10 | GF-03 | SD-250 | 170 L/s | 26 | 2.6 |
| SD-FF-01 | FF-03 | SD-250 | 158 L/s | 24 | 2.4 |
| SD-FF-02 | FF-03 | SD-250 | 158 L/s | 24 | 2.4 |
| SD-FF-03 | FF-04 | SD-150 | 63 L/s | 22 | 1.5 |
| SD-FF-04 | FF-10 | SD-200 | 125 L/s | 27 | 2.3 |
| SD-FF-05 | FF-10 | SD-200 | 125 L/s | 27 | 2.3 |
| SD-FF-06 | FF-10 | SD-200 | 125 L/s | 27 | 2.3 |
| SD-FF-07 | FF-11 | SD-150 | 43 L/s | 15 | 1.0 |
| SD-FF-08 | FF-07 | SD-150 | 43 L/s | 15 | 1.0 |
| SD-FF-09 | FF-08 | SD-150 | 57 L/s | 20 | 1.4 |
| SD-FF-10 | FF-05 | SD-150 | 60 L/s | 21 | 1.4 |
| SD-FF-11 | FF-05 | SD-150 | 60 L/s | 21 | 1.4 |
| SD-FF-12 | FF-09 | SD-200 | 113 L/s | 24 | 2.1 |

Code reference: ASHRAE Applications 2019 Ch.49 Table 1 (design NC)

## 6.2 Exhaust systems

| Fan | Room | Flow | Model | Duct | Length m | Velocity | ESP req. | Discharge | Clause |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| EF-GF-01 | GF-06 | 50 L/s | EF-50 | Ø150 | 4.41 | 2.83 m/s | 46 Pa | wall_louver | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| EF-GF-02 | GF-09 | 25 L/s | EF-25 | Ø125 | 1.48 | 2.04 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-GF-03 | GF-11 | 25 L/s | EF-25 | Ø125 | 1.12 | 2.04 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-GF-04 | GF-13 | 25 L/s | EF-25 | Ø125 | 1.78 | 2.04 m/s | 42 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-FF-01 | FF-01 | 25 L/s | EF-25 | Ø125 | 2.27 | 2.04 m/s | 42 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-FF-02 | FF-02 | 25 L/s | EF-25 | Ø125 | 1.22 | 2.04 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-FF-03 | FF-12 | 25 L/s | EF-25 | Ø125 | 1.48 | 2.04 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-FF-04 | FF-14 | 25 L/s | EF-25 | Ø125 | 1.24 | 2.04 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |

# 7. Piping

## 7.1 Refrigerant piping

| Run | Unit → ODU | Capacity | Liquid / gas OD mm | Horiz. floor m | Vertical m | Roof m | Total m | Limit m | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| RP-IU-GF-01 | IU-GF-01 → ODU-01 | 5.3 kW | 6.35 / 12.7 (1/4" / 1/2") | 10.39 | 8.7 | 0.65 | 21.7 | 25 | OK |
| RP-IU-GF-02 | IU-GF-02 → ODU-02 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 2.63 | 8.7 | 1.9 | 14.6 | 25 | OK |
| RP-IU-GF-03 | IU-GF-03 → ODU-03 | 7.0 kW | 9.52 / 15.88 (3/8" / 5/8") | 15.51 | 8.7 | 2.2 | 29.1 | 50 | OK |
| RP-IU-GF-04 | IU-GF-04 → ODU-04 | 14.0 kW | 9.52 / 15.88 (3/8" / 5/8") | 13.09 | 8.7 | 3.45 | 27.8 | 50 | OK |
| RP-IU-FF-01 | IU-FF-01 → ODU-05 | 7.0 kW | 9.52 / 15.88 (3/8" / 5/8") | 14.39 | 5.1 | 3.5 | 25.3 | 50 | OK |
| RP-IU-FF-02 | IU-FF-02 → ODU-06 | 14.0 kW | 9.52 / 15.88 (3/8" / 5/8") | 13.09 | 5.1 | 3.75 | 24.1 | 50 | OK |

Code reference: SBC 501 Ch.11 §1107 (refrigerant piping); ASHRAE 15; manufacturer piping tables

## 7.3 Condensate drains

| Run | Unit | To | Code min mm | Design mm | Length m | Slope % |
| --- | --- | --- | --- | --- | --- | --- |
| CD-IU-GF-01 | IU-GF-01 | GF-06 KITCHEN (floor drain / waste stack with trap) | 20 | 25 | 2.54 | 1.0 |
| CD-IU-GF-02 | IU-GF-02 | GF-10 SHAFT (floor drain / waste stack with trap) | 20 | 25 | 2.9 | 1.0 |
| CD-IU-GF-03 | IU-GF-03 | GF-06 KITCHEN (floor drain / waste stack with trap) | 20 | 25 | 8.14 | 1.0 |
| CD-IU-GF-04 | IU-GF-04 | GF-06 KITCHEN (floor drain / waste stack with trap) | 20 | 25 | 5.48 | 1.0 |
| CD-IU-FF-01 | IU-FF-01 | FF-01 MASTER BATH (floor drain / waste stack with trap) | 20 | 25 | 2.69 | 1.0 |
| CD-IU-FF-02 | IU-FF-02 | FF-01 MASTER BATH (floor drain / waste stack with trap) | 20 | 25 | 6.24 | 1.0 |

Code reference: SBC 501 §307.2.1 (disposal), §307.2.2 Table 307.2.2 (drain size), slope >= 1 %

# 8. Design checks

| Check | Status | Detail |
| --- | --- | --- |
| Every room served | PASS | 16 conditioned rooms served, 8 exhaust rooms; not served by design (stores/shafts): GF-10, GF-12, FF-06, FF-13 |
| No duct crossing shaft/stair/column unresolved | PASS | trunk routes chosen clear of shafts, stairs (not served) and columns; beams not on plan - coordinate |
| Airflows balance | PASS | supply = unit airflow in all ducted zones; building OA 274.9 L/s vs exhaust 225.0 L/s (net +50 L/s) |
| All items tagged (unique) | PASS | 73 tags |
| Every drawing item in BOQ | PASS | 85 drawn tags all in BOQ (pipe runs 6 measured by size in section G) |
| Unit external static pressure | PASS | all ducted units have ESP margin |
| Refrigerant length / height limits | PASS | within generic limits (verify with brand) |
| Diffuser noise (NC) | PASS | all diffusers at or below room NC target |
| Fresh-air fraction | PASS | OA fraction within limit for untreated fresh air |
| Open questions | PASS | none |

# 9. Code clause register

| Rule | Clause applied |
| --- | --- |
| design_conditions | SBC 602 §302 / SBC 601 §302.1 (design conditions); ASHRAE Fundamentals 2021 Ch.14 (0.4 % cooling, 99.6 % heating) |
| envelope_u | SBC 602 Ch.4 prescriptive envelope table / SBC 601 Ch.5 (max U-factor, SHGC) |
| load_method | ASHRAE Fundamentals 1997 Ch.28 CLTD/SCL/CLF method, Tables 30-36 |
| infiltration | ASHRAE Fundamentals 2021 Ch.16 §'Residential air change method' |
| internal_gains | ASHRAE Fundamentals 2021 Ch.18 Table 1 (people), Tables 2-3 (lighting), Tables 5-9 (equipment) |
| oa_rate | SBC 501 §403.3.1.1 & Table 403.3.1.1; ASHRAE 62.1-2019 §6.2.2.1 Eq.6-1, Table 6-1 |
| oa_zone_eff | ASHRAE 62.1-2019 §6.2.2.2 Table 6-2 (Ez) |
| oa_system_eff | ASHRAE 62.1-2019 §6.2.4.3.1 simplified procedure (Ev) |
| exhaust_toilet | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| exhaust_kitchen | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| exhaust_toilet_public | ASHRAE 62.1-2019 Table 6-4 (toilet public: 25 L/s per WC/urinal) |
| duct_sizing | ASHRAE Fundamentals 2021 Ch.21 (equal friction method, Eq.18-19 Altshul-Tsal) |
| duct_construction | SBC 501 §603.4 metallic ducts; SMACNA 2005 Tables 2-1/2-2 (gauge) |
| duct_insulation | SBC 601 §C403.11.1 / ASHRAE 90.1-2019 §6.4.4.1.2, Table 6.8.2 |
| pipe_insulation | SBC 601 §C403.11.3 / ASHRAE 90.1-2019 §6.4.4.1.3, Table 6.8.3-1/-2 |
| refrigerant_piping | SBC 501 Ch.11 §1107 (refrigerant piping); ASHRAE 15; manufacturer piping tables |
| chw_piping | ASHRAE Fundamentals 2021 Ch.22 (water velocity / friction limits) |
| condensate | SBC 501 §307.2.1 (disposal), §307.2.2 Table 307.2.2 (drain size), slope >= 1 % |
| equipment_efficiency | SASO 2663 / SBC 601 Table C403.3.2 minimum efficiency |
| noise | ASHRAE Applications 2019 Ch.49 Table 1 (design NC) |
| safety_factor | Designer allowance - not a code requirement |
| controls | SBC 601 §C403.4 / ASHRAE 90.1 §6.4.3 (thermostatic controls, OA damper shut-off) |

# Appendix - sample sheet (M-101)