HVAC DESIGN CALCULATION REPORT

DDA MIG Housing Scheme 182A (test run under KSA codes)

Riyadh, Saudi Arabia

Building type: apartment - 4 floor(s)

Code basis: Saudi Building Code + ASHRAE   |   Units: SI

Issue: P0 (preliminary)   2026-10-15

PRELIMINARY DESIGN - FOR COORDINATION ONLY. To be checked and stamped by a qualified HVAC engineer before construction.

# 1. Design basis

## 1.1 Codes and standards

| Ref | Code / standard |
| --- | --- |
| SBC501 | SBC 501 Saudi Mechanical Code (2018, as amended) |
| SBC601 | SBC 601 Saudi Energy Conservation Code - Commercial |
| SBC602 | SBC 602 Saudi Energy Conservation Code - Residential |
| A62.1 | ANSI/ASHRAE Standard 62.1-2019 Ventilation for Acceptable IAQ |
| A90.1 | ANSI/ASHRAE/IES Standard 90.1-2019 Energy Standard |
| AF | ASHRAE Handbook - Fundamentals (CLTD/SCL/CLF method 1997 Ch.28; climate data 2021 Ch.14) |
| SMACNA | SMACNA HVAC Duct Construction Standards - Metal and Flexible, 3rd ed. 2005 |

## 1.2 Design conditions

| Parameter | Value | Basis |
| --- | --- | --- |
| Outdoor summer design (0.4 %) | 45.6 °C DB / 19.4 °C MCWB, W = 4.4 g/kg | ASHRAE 2021 Ch.14 (0.4% cool / 99.6% heat) - OERK |
| Daily range | 14.6 K | ASHRAE 2021 Ch.14 (0.4% cool / 99.6% heat) - OERK |
| Outdoor winter design (99.6 %) | 6.6 °C | ASHRAE 2021 Ch.14 (0.4% cool / 99.6% heat) - OERK |
| Indoor cooling | 24.0 °C, 50 % RH (W = 10.0 g/kg) | SBC 602 §302 / SBC 601 §302.1 (design conditions); ASHRAE Fundamentals 2021 Ch.14 (0.4 % cooling, 99.6 % heating) |
| Indoor heating | 21.0 °C | SBC 602 §302 / SBC 601 §302.1 (design conditions); ASHRAE Fundamentals 2021 Ch.14 (0.4 % cooling, 99.6 % heating) |
| Site elevation / pressure | 612 m / 94.19 kPa; air factors 1.143 W/(L/s·K), 2798 W/(L/s·kg/kg) | ASHRAE Fundamentals Ch.1 |
| Latitude / design month | 24.71° / July (CLTD tables) | ASHRAE Fundamentals 1997 Ch.28 CLTD/SCL/CLF method, Tables 30-36 |

Code reference: SBC 602 §302 / SBC 601 §302.1 (design conditions); ASHRAE Fundamentals 2021 Ch.14 (0.4 % cooling, 99.6 % heating)

## 1.3 Building envelope

| Element | U-value / property | Basis |
| --- | --- | --- |
| External wall | 0.40 W/m²K (CLTD wall group D) | SBC602 |
| Roof | 0.20 W/m²K (roof_insulated_concrete) | SBC602 |
| Glazing | 2.67 W/m²K, SHGC 0.25 (SC 0.29) | SBC602 |
| Slab edge (heating) | F = 1.2 W/m·K | SBC602 |

Code reference: SBC 602 Ch.4 prescriptive envelope table / SBC 601 Ch.5 (max U-factor, SHGC)

## 1.4 Internal loads

| Space type | Occupancy | Activity | Lighting W/m² | Equipment W/m² + fixed | OA category | Exhaust | Cooled |
| --- | --- | --- | --- | --- | --- | --- | --- |
| bath | 0 persons | seated | 8 | 0 + 0 W |  | toilet_private | no |
| bedroom | 2 persons | sleeping | 8 | 5 + 0 W | dwelling |  | yes |
| dining | 2.5 m²/person | seated | 10 | 3 + 0 W | dwelling |  | yes |
| kitchen | 2 persons | light_work | 10 | 60 + 800 W | dwelling | kitchen_residential | yes |
| outdoor | 0 persons | seated | 0 | 0 + 0 W |  |  | no |
| shaft | 0 persons | seated | 0 | 0 + 0 W |  |  | no |

Code reference: ASHRAE Fundamentals 2021 Ch.18 Table 1 (people), Tables 2-3 (lighting), Tables 5-9 (equipment)

## 1.5 Assumptions

All assumptions are logged in assumptions.md. Items marked 'confirm' must be confirmed by the engineer of record.

| ID | Step | Assumption | Source | Status |
| --- | --- | --- | --- | --- |
| A001 | A-read | Window W1 size 600x600 mm given by user (not in schedule) | user | default |
| A002 | A-read | Page 1 scale 1:139.0 (user, confidence high) | scale_detect.py | default |
| A003 | Gate1 | Page 1 TERRACE: measured 6.06 m² vs plan text 7.36 m² (>12% difference). Which is right? -> USER ANSWER: use measured | user | default |
| A004 | Gate1 | Page 1 DINNING /LOUNGE: measured 22.82 m² vs plan text 11.14 m² (>12% difference). Which is right? -> USER ANSWER: drawing room + dining/lounge are open plan - one living zone ~18 m2 (measured) | user | default |
| A005 | Gate1 | Page 1 KITCHEN: measured 4.24 m² vs plan text 4.85 m² (>12% difference). Which is right? -> USER ANSWER: use measured | user | default |
| A006 | Gate1 | Page 1 BATH: measured 1.59 m² vs plan text 1.85 m² (>12% difference). Which is right? -> USER ANSWER: use measured | user | default |
| A007 | Gate1 | Page 1 SHAFT: measured 2.69 m² vs plan text 3.11 m² (>12% difference). Which is right? -> USER ANSWER: use measured | user | default |
| A008 | Gate1 | Page 1 ROOM: measured 7.57 m² vs plan text 9.06 m² (>12% difference). Which is right? -> USER ANSWER: use measured (traced drawing) | user | default |
| A009 | A-read | Page 1: 36 labelled cells ignored as non-rooms (schedule/title/grid text): ['3.TERRACE', 'CB', 'D D A', 'DILSHAD GARDEN', 'DINNING /LOUNGE', 'Digitized By', 'EAST ZONE, VIKAS MINAR, D.D.A.', 'FG1', 'GROUND AND FIRST', 'JAHANGIRPURI', 'PASHCHIM PURI', 'PITAMPURA (D&P)', 'SHALIMAR BHAGH (P)', 'STANDARD DESIGN FOR MIG', 'Sch.no. 182A'] | pdf_reader.py | default |
| A010 | Gate1 | Page 1: 15 enclosed space(s) without a name (areas m²: [1.61, 1.71, 1.71, 3.26, 2.23, 1.71, 1.7, 1.7, 1.7, 2.26, 3.29, 1.71, 1.71, 2.66, 1.61]). Name them or confirm they are voids. -> USER ANSWER: small unnamed spaces are flat entrance lobbies/passages - not cooled, transfer air | user | default |
| A011 | A-read | Page 1: 'GROUND FLOOR PLAN' plan separated from the other plan(s) on the sheet by nearest title | pdf_reader.py | default |
| A012 | A-read | Page 1: 'FIRST FLOOR PLAN' plan separated from the other plan(s) on the sheet by nearest title | pdf_reader.py | default |
| A013 | A-read | Page 2 scale 1:139.0 (user, confidence high) | scale_detect.py | default |
| A014 | Gate1 | Page 2 ROOM: measured 10.18 m² vs plan text 9.06 m² (>12% difference). Which is right? -> USER ANSWER: use measured | user | default |
| A015 | Gate1 | Page 2 DINNING /LOUNGE: measured 22.92 m² vs plan text 11.14 m² (>12% difference). Which is right? -> USER ANSWER: same - one living zone | user | default |
| A016 | Gate1 | Page 2 KITCHEN: measured 5.74 m² vs plan text 4.85 m² (>12% difference). Which is right? -> USER ANSWER: use measured | user | default |
| A017 | Gate1 | Page 2: one enclosed space carries several names ['SHAFT', 'SHAFT'] - an opening may be unsealed. Split or confirm. -> USER ANSWER: two shaft labels in one light well - one shaft | user | default |
| A018 | Gate1 | Page 2 TERRACE: measured 9.24 m² vs plan text 7.36 m² (>12% difference). Which is right? -> USER ANSWER: use measured | user | default |
| A019 | Gate1 | Page 2 SHAFT: measured 3.65 m² vs plan text 3.11 m² (>12% difference). Which is right? -> USER ANSWER: use measured | user | default |
| A020 | Gate1 | Page 2 BATH: measured 2.08 m² vs plan text 1.85 m² (>12% difference). Which is right? -> USER ANSWER: use measured | user | default |
| A021 | A-read | Page 2: 33 labelled cells ignored as non-rooms (schedule/title/grid text): ['CB', 'D D A', 'DILSHAD GARDEN', 'Digitized By', 'EAST ZONE, VIKAS MINAR, D.D.A.', 'FG1', 'JAHANGIRPURI', 'PASHCHIM PURI', 'PITAMPURA (D&P)', 'SECOND AND THIRD', 'SHALIMAR BHAGH (P)', 'STANDARD DESIGN FOR MIG', 'Sch.no. 182A', 'TERRACE', 'WING'] | pdf_reader.py | default |
| A022 | Gate1 | Page 2: 9 enclosed space(s) without a name (areas m²: [2.41, 2.42, 3.46, 3.53, 3.7, 3.44, 3.52, 2.42, 2.42]). Name them or confirm they are voids. -> USER ANSWER: same - passages | user | default |
| A023 | A-read | Page 2: 'SECOND FLOOR PLAN' plan separated from the other plan(s) on the sheet by nearest title | pdf_reader.py | default |
| A024 | A-read | Page 2: 'THIRD FLOOR PLAN' plan separated from the other plan(s) on the sheet by nearest title | pdf_reader.py | default |
| A025 | A-read | Page 3 scale 1:139.0 (user, confidence high) | scale_detect.py | default |
| A026 | Gate1 | Page 3 SHAFT: measured 3.65 m² vs plan text 3.11 m² (>12% difference). Which is right? -> USER ANSWER: use measured | user | default |
| A027 | A-read | Page 3: 22 labelled cells ignored as non-rooms (schedule/title/grid text): ['D D A', 'Digitized By', 'SLOPE', 'STANDARD DESIGN FOR MIG', 'Sch.no. 182A', 'WING', 'WITH SA VIDE LETTER NO.ACE/D/III/S.D/9/E', 'add. ch. arch.', 'arch. asstt.', 'asstt. arch.', 'asstt. dir.', 'chief arch.', 'deputy director'] | pdf_reader.py | default |
| A028 | Gate1 | Page 3: 8 enclosed space(s) without a name (areas m²: [2.4, 2.32, 3.5, 2.91, 2.29, 2.13, 3.53, 2.42]). Name them or confirm they are voids. -> USER ANSWER: same - passages / mumty | user | default |
| A029 | Gate1 | Second Floor: 4 rooms copied from Third Floor where the plan did not read (typical flats): SF-34 BALCONY (TF-02), SF-35 BALCONY (TF-03), SF-36 BALCONY (TF-32), SF-37 BALCONY (TF-33) | user instruction | CONFIRM |
| A030 | B-loads | Outdoor design 45.6 °C DB / 19.4 °C MCWB (0.4 %), daily range 14.6 K, heating 6.6 °C (99.6 %), elevation 612.0 m (ASHRAE 2021 Ch.14 (0.4% cool / 99.6% heat) - OERK, approximate - verify) | references/climate_data.csv | default |
| A031 | B-loads | Indoor design 24.0 °C / 50 % RH cooling, 21.0 °C heating | SBC 602 §302 / SBC 601 §302.1 (design conditions); ASHRAE Fundamentals 2021 Ch.14 (0.4 % cooling, 99.6 % heating) | default |
| A032 | B-loads | Envelope U-values = code maximum (SBC602: wall 0.4, roof 0.2, glazing U 2.67 / SHGC 0.25 W/m²K) - actual build-up not given | SBC 602 Ch.4 prescriptive envelope table / SBC 601 Ch.5 (max U-factor, SHGC) | CONFIRM |
| A033 | B-loads | Cooling loads by CLTD/SCL/CLF; CLTD tables for wall group D, roof 'roof_insulated_concrete', latitude row nearest 24.71°, July; colour factor K=0.83 (medium walls), roof K=1.0; glass with interior shading=True | ASHRAE Fundamentals 1997 Ch.28 CLTD/SCL/CLF method, Tables 30-36 | CONFIRM |
| A034 | B-loads | CLTD/LM/SHGF/CLF tables in references/cltd_tables.json are transcribed-approximate - verify against licensed ASHRAE 1997 Ch.28 tables | references/cltd_tables.json | CONFIRM |
| A035 | B-loads | CLF for people/lights/equipment = 1.0 (24 h operation, no storage credit) | ASHRAE Fundamentals 1997 Ch.28 CLTD/SCL/CLF method, Tables 30-36 | default |
| A036 | B-loads | Partitions/floors between conditioned and exhaust-only rooms (baths, stores) not counted: those rooms are near room temperature | designer judgement | default |
| A037 | B-loads | Outdoor humidity ratio 4.4 g/kg < indoor 10.0 g/kg at design: outdoor-air latent load taken as 0 (conservative); check a dehumidification design day | ASHRAE Fundamentals 2021 Ch.14 (DP design) | CONFIRM |
| A038 | B-loads | Conditioned/unconditioned overrides from the user: by type {'kitchen': False}, by room {} | user instruction | default |
| A039 | B-loads | Supply air 13.0 °C (room-supply ΔT 11.0 K) for airflow | designer default | default |
| A040 | B-loads | Infiltration by air-change method: {'one_exterior_side': 0.5, 'two_plus_exterior_sides': 0.75, 'no_exterior': 0.0} ACH (residential) | ASHRAE Fundamentals 2021 Ch.16 §'Residential air change method' | default |
| A041 | B-loads | Occupancy, lighting and equipment densities from references/space_types.json | ASHRAE Fundamentals 2021 Ch.18 Table 1 (people), Tables 2-3 (lighting), Tables 5-9 (equipment) | default |
| A042 | B-zoning | Zoning: own zone for ['majlis', 'master_bedroom']; other ducted rooms grouped by position per floor up to 17.6 kW per unit (incl. safety factor) | references/design_defaults.json zoning | CONFIRM |
| A043 | B-zoning | Rooms exhaust-only (not cooled; make-up by transfer air): GF-04, GF-05, GF-06, GF-08, GF-09, GF-17, GF-18, GF-19, GF-21, GF-22, GF-23, GF-33, GF-34, GF-36, GF-37, FF-07, FF-08, FF-09, FF-11, FF-12, FF-13, FF-18, FF-19, FF-20, FF-22, FF-23, FF-24, SF-05, SF-07, SF-09, SF-11, SF-12, SF-13, SF-14, SF-20, SF-21, SF-23, SF-25, SF-27, SF-29, TF-07, TF-09, TF-11, TF-13, TF-14, TF-15, TF-19, TF-20, TF-22, TF-24, TF-26, TF-28 | references/space_types.json | CONFIRM |
| A044 | B-vent | Zone air distribution effectiveness Ez = 0.8 (heat-pump heating with ceiling supply of warm air) | ASHRAE 62.1-2019 §6.2.2.2 Table 6-2 (Ez) | default |
| A045 | B-vent | Exhaust fans sized for the intermittent (rated) rate; continuous operation would allow the lower rate | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) | default |
| A046 | B-vent | Building OA 891 L/s < exhaust 1725 L/s (intermittent): building slightly negative when all fans run; acceptable for intermittent fans, else raise OA | designer judgement | CONFIRM |
| A047 | B-equip | Safety factor 10% on cooling and 10% on heating, applied to coil loads at selection (shown in tables) | Designer allowance - not a code requirement | CONFIRM |
| A048 | B-equip | Nominal (T1) capacities derated x0.88 for 45.6 °C outdoor design (T3) - replace with brand T3 data | references/equipment_catalog.json t3_derate | CONFIRM |
| A049 | B-equip | Equipment from GENERIC catalogue (references/equipment_catalog.json) - replace with the approved brand | references/equipment_catalog.json | CONFIRM |
| A050 | B-equip | Minimum supply per served room 30 L/s (smallest diffuser) | references/air_terminals.json | default |
| A051 | B-equip | IU-GF-01 (WS-09) is 194 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A052 | B-equip | IU-GF-02 (WS-09) is 215 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A053 | B-equip | IU-GF-03 (WS-09) is 193 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A054 | B-equip | IU-GF-04 (WS-09) is 184 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A055 | B-equip | IU-GF-05 (WS-09) is 192 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A056 | B-equip | IU-GF-06 (WS-09) is 226 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A057 | B-equip | IU-GF-07 (WS-09) is 204 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A058 | B-equip | IU-GF-08 (WS-09) is 178 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A059 | B-equip | IU-GF-09 (DS-18) is 76 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A060 | B-equip | Z-GF-09: no corridor/service room next to the zone - ducted unit in the DINNING /LOUNGE (GF-25) ceiling void, access panel required | designer judgement | CONFIRM |
| A061 | B-equip | IU-GF-10 (DS-18) is 72 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A062 | B-equip | Z-GF-10: no corridor/service room next to the zone - ducted unit in the DINNING /LOUNGE (GF-26) ceiling void, access panel required | designer judgement | CONFIRM |
| A063 | B-equip | IU-GF-11 (DS-18) is 81 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A064 | B-equip | Z-GF-11: no corridor/service room next to the zone - ducted unit in the DINNING /LOUNGE (GF-31) ceiling void, access panel required | designer judgement | CONFIRM |
| A065 | B-equip | IU-GF-12 (DS-18) is 78 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A066 | B-equip | Z-GF-12: no corridor/service room next to the zone - ducted unit in the DINNING /LOUNGE (GF-32) ceiling void, access panel required | designer judgement | CONFIRM |
| A067 | B-equip | IU-FF-01 (WS-09) is 95 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A068 | B-equip | IU-FF-02 (WS-09) is 129 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A069 | B-equip | IU-FF-03 (WS-09) is 178 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A070 | B-equip | IU-FF-04 (WS-09) is 192 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A071 | B-equip | IU-FF-05 (WS-09) is 177 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A072 | B-equip | IU-FF-06 (WS-09) is 191 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A073 | B-equip | IU-FF-07 (WS-09) is 97 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A074 | B-equip | IU-FF-08 (WS-09) is 131 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A075 | B-equip | IU-FF-09 (DS-18) is 81 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A076 | B-equip | Z-FF-09: no corridor/service room next to the zone - ducted unit in the DINNING /LOUNGE (FF-04) ceiling void, access panel required | designer judgement | CONFIRM |
| A077 | B-equip | IU-FF-10 (DS-18) is 78 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A078 | B-equip | Z-FF-10: no corridor/service room next to the zone - ducted unit in the DINNING /LOUNGE (FF-05) ceiling void, access panel required | designer judgement | CONFIRM |
| A079 | B-equip | IU-FF-11 (DS-18) is 76 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A080 | B-equip | Z-FF-11: no corridor/service room next to the zone - ducted unit in the DINNING /LOUNGE (FF-26) ceiling void, access panel required | designer judgement | CONFIRM |
| A081 | B-equip | IU-FF-12 (DS-18) is 76 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A082 | B-equip | Z-FF-12: no corridor/service room next to the zone - ducted unit in the DINNING /LOUNGE (FF-27) ceiling void, access panel required | designer judgement | CONFIRM |
| A083 | B-equip | IU-SF-01 (WS-09) is 150 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A084 | B-equip | IU-SF-02 (WS-09) is 157 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A085 | B-equip | IU-SF-03 (WS-09) is 217 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A086 | B-equip | IU-SF-04 (WS-09) is 130 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A087 | B-equip | IU-SF-05 (WS-09) is 153 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A088 | B-equip | IU-SF-06 (WS-09) is 130 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A089 | B-equip | IU-SF-07 (WS-09) is 152 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A090 | B-equip | IU-SF-08 (WS-09) is 132 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A091 | B-equip | IU-SF-09 (WS-09) is 138 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A092 | B-equip | Z-SF-10: no corridor/service room next to the zone - ducted unit in the DINNING /LOUNGE (SF-06) ceiling void, access panel required | designer judgement | CONFIRM |
| A093 | B-equip | Z-SF-11: no corridor/service room next to the zone - ducted unit in the DINNING /LOUNGE (SF-10) ceiling void, access panel required | designer judgement | CONFIRM |
| A094 | B-equip | Z-SF-12: no corridor/service room next to the zone - ducted unit in the DINNING /LOUNGE (SF-24) ceiling void, access panel required | designer judgement | CONFIRM |
| A095 | B-equip | Z-SF-13: no corridor/service room next to the zone - ducted unit in the DINNING /LOUNGE (SF-28) ceiling void, access panel required | designer judgement | CONFIRM |
| A096 | B-equip | IU-TF-01 (WS-09) is 98 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A097 | B-equip | IU-TF-02 (WS-09) is 118 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A098 | B-equip | IU-TF-03 (WS-09) is 116 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A099 | B-equip | IU-TF-04 (WS-09) is 137 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A100 | B-equip | IU-TF-05 (WS-09) is 115 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A101 | B-equip | IU-TF-06 (WS-09) is 135 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A102 | B-equip | IU-TF-07 (WS-09) is 99 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A103 | B-equip | IU-TF-08 (WS-09) is 103 % above requirement - smallest catalogue size; consider combining zones or a smaller (VRF/wall) unit | designer note | CONFIRM |
| A104 | B-equip | Z-TF-09: no corridor/service room next to the zone - ducted unit in the DINNING /LOUNGE (TF-08) ceiling void, access panel required | designer judgement | CONFIRM |
| A105 | B-equip | Z-TF-10: no corridor/service room next to the zone - ducted unit in the DINNING /LOUNGE (TF-12) ceiling void, access panel required | designer judgement | CONFIRM |
| A106 | B-equip | Z-TF-11: no corridor/service room next to the zone - ducted unit in the DINNING /LOUNGE (TF-23) ceiling void, access panel required | designer judgement | CONFIRM |
| A107 | B-equip | Z-TF-12: no corridor/service room next to the zone - ducted unit in the DINNING /LOUNGE (TF-27) ceiling void, access panel required | designer judgement | CONFIRM |
| A108 | B-equip | Wall-split outdoor units on brackets on the facade/courtyard wall just outside the served room (architect to approve appearance); ducted-unit ODUs on the roof | user preference | CONFIRM |
| A109 | B-equip | Outdoor units grouped on the roof near the riser/shaft with 0.6 m service clearance; check structure, parapet height and acoustic screening | designer judgement | CONFIRM |
| A110 | B-ducts | Ducts sized by equal friction 0.8 Pa/m with velocity limits {'main': 5.0, 'branch': 3.5, 'runout': 2.5, 'return': 3.5, 'fresh_air': 4.0, 'exhaust': 4.0} m/s; max duct depth 250 mm from ceiling void | ASHRAE Fundamentals 2021 Ch.21 (equal friction method, Eq.18-19 Altshul-Tsal) | default |
| A111 | B-ducts | Fittings allowed as +50% equivalent length; unit plenum/filter 40.0 Pa | designer default | CONFIRM |
| A112 | B-ducts | Duct routes are schematic trunk-and-branch lines over the plan; coordinate with structure (beams), lighting and other services | designer judgement | CONFIRM |
| A113 | B-ducts | Return air from rooms via door undercut / door transfer grilles to the return grille near the unit | ASHRAE Fundamentals 2021 Ch.21 (equal friction method, Eq.18-19 Altshul-Tsal) | CONFIRM |
| A114 | B-pipes | Refrigerant pipe sizes from GENERIC table (references/pipe_sizing.json) - replace with the selected brand's table | SBC 501 Ch.11 §1107 (refrigerant piping); ASHRAE 15; manufacturer piping tables | CONFIRM |
| A115 | B-pipes | Refrigerant length = route x (1+10%) + vertical rise to roof (+1.5 m allowance) | designer default | default |
| A116 | B-pipes | Condensate to nearest wet-room floor drain / stack with trap; min 25 mm, slope 1.0 % | SBC 501 §307.2.1 (disposal), §307.2.2 Table 307.2.2 (drain size), slope >= 1 % | CONFIRM |

# 2. Room schedule (Gate 1 approved)

| ID | Room | Type | Area m² | Ceiling m | Exterior walls (orient. m) | Windows | Roof exp. | Cooled |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| GF-01 | VER. | outdoor | 3.58 | 2.75 | N 3.05, E 1.17 | W3A E 0.575x1.175 | 100% | no |
| GF-02 | ROOM | bedroom | 8.12 | 2.75 | N 3.02 | W3A N 0.575x1.175 | 40% | yes |
| GF-03 | ROOM | bedroom | 8.13 | 2.75 | N 2.98 | - | 41% | yes |
| GF-04 | KITCHEN | kitchen | 4.30 | 2.75 | S 1.63 | - | 0% | yes |
| GF-05 | BATH | bath | 1.59 | 2.75 | E 1.19 | - | 0% | no |
| GF-06 | WC | bath | 1.57 | 2.75 | N 0.92 | W1 N 1.2x1.54 | 0% | no |
| GF-07 | SHAFT | shaft | 2.69 | 2.75 | - | - | 83% | no |
| GF-08 | WC | bath | 1.57 | 2.75 | N 0.88 | W1 N 1.2x1.54 | 0% | no |
| GF-09 | BATH | bath | 1.63 | 2.75 | W 1.32 | - | 0% | no |
| GF-10 | COURTYARD | outdoor | 11.51 | 2.75 | S 4.37, W 4.13, E 1.63 | W3A S 0.575x1.175 | 74% | no |
| GF-11 | ROOM | bedroom | 8.05 | 2.75 | E 2.67 | W3A E 0.575x1.175 | 0% | yes |
| GF-12 | COURTYARD | outdoor | 12.30 | 2.75 | E 4.24, S 4.3, W 1.63 | - | 75% | no |
| GF-13 | COURTYARD | outdoor | 12.34 | 2.75 | N 4.26, W 4.25, E 1.62 | - | 100% | no |
| GF-14 | ROOM | bedroom | 7.57 | 2.75 | W 2.68 | W3A W 0.575x1.175 | 0% | yes |
| GF-15 | ROOM | bedroom | 8.07 | 2.75 | E 2.67 | W3A E 0.575x1.175 | 0% | yes |
| GF-16 | COURTYARD | outdoor | 11.62 | 2.75 | N 4.26, E 4.12, W 1.62 | - | 100% | no |
| GF-17 | KITCHEN | kitchen | 4.22 | 2.75 | N 1.63 | W4 N 0.575x1.175 | 42% | yes |
| GF-18 | BATH | bath | 1.59 | 2.75 | E 1.22 | - | 0% | no |
| GF-19 | WC | bath | 1.56 | 2.75 | S 0.89 | - | 0% | no |
| GF-20 | SHAFT | shaft | 2.75 | 2.75 | W 0.54 | W1 W 1.2x1.54, W1 W 1.2x1.54 | 0% | no |
| GF-21 | WC | bath | 1.56 | 2.75 | S 0.77 | - | 0% | no |
| GF-22 | BATH | bath | 1.62 | 2.75 | W 1.3 | - | 0% | no |
| GF-23 | KITCHEN | kitchen | 4.24 | 2.75 | N 1.65 | W4 N 0.575x1.175 | 43% | yes |
| GF-24 | ROOM | bedroom | 8.12 | 2.75 | S 3.01 | - | 0% | yes |
| GF-25 | DINNING /LOUNGE | dining | 18.44 | 2.75 | N 1.45, S 2.67, W 0.78 | W3A S 0.575x1.175, W2 N 0.575x1.175 | 11% | yes |
| GF-26 | DINNING /LOUNGE | dining | 18.40 | 2.75 | N 1.43, E 0.8, S 2.65, W 2.32 | W3A S 0.575x1.175, W2 N 0.575x1.175 | 12% | yes |
| GF-27 | ROOM | bedroom | 8.13 | 2.75 | S 2.99 | W3A S 0.575x1.175 | 0% | yes |
| GF-28 | VER. | outdoor | 3.69 | 2.75 | S 2.28, W 1.19 | W3A W 0.575x1.175 | 22% | no |
| GF-29 | VER. | outdoor | 3.58 | 2.75 | S 3.06 | - | 23% | no |
| GF-30 | TERRACE | outdoor | 6.06 | 2.75 | N 2.39, E 0.66, W 1.9 | W3A W 0.575x1.175 | 100% | no |
| GF-31 | DINNING /LOUNGE | dining | 18.13 | 2.75 | N 2.67, S 1.68, W 0.81 | W3A N 0.575x1.175 | 0% | yes |
| GF-32 | DINNING /LOUNGE | dining | 18.20 | 2.75 | N 2.68, E 0.79, S 1.68 | W3A N 0.575x1.175 | 23% | yes |
| GF-33 | BATH | bath | 1.58 | 2.75 | E 1.18 | - | 0% | no |
| GF-34 | WC | bath | 1.55 | 2.75 | N 0.85 | W1 N 1.2x1.54 | 0% | no |
| GF-35 | SHAFT | shaft | 2.67 | 2.75 | - | - | 27% | no |
| GF-36 | BATH | bath | 1.62 | 2.75 | W 1.32 | - | 31% | no |
| GF-37 | KITCHEN | kitchen | 4.48 | 2.75 | E 2.6, S 1.63 | W1 E 1.2x1.54 | 0% | yes |
| GF-38 | ROOM | bedroom | 7.94 | 2.75 | W 2.6 | W3A W 0.575x1.175 | 12% | yes |
| GF-39 | SHAFT | shaft | 2.63 | 2.75 | W 0.27 | W1 W 1.2x1.54 | 3% | no |
| GF-40 | TERRACE | outdoor | 5.98 | 2.75 | NW 0.09, W 2.29, S 3.01, E 0.81 | W3A NW 0.575x1.175 | 0% | no |
| GF-41 | TERRACE | outdoor | 6.38 | 2.75 | E 1.91, S 3.54, W 0.93 | W3A E 0.575x1.175 | 0% | no |
| FF-01 | TERRACE | outdoor | 6.06 | 2.75 | N 2.39, E 0.66, W 1.9 | W3A W 0.575x1.175 | 100% | no |
| FF-02 | TERRACE | outdoor | 6.54 | 2.75 | N 3.26, E 2.1, W 0.93 | W3A E 0.575x1.175 | 82% | no |
| FF-03 | ROOM | bedroom | 8.11 | 2.75 | N 3.0, W 2.6 | W1 W 1.2x1.54 | 5% | yes |
| FF-04 | DINNING /LOUNGE | dining | 18.13 | 2.75 | N 2.67, S 1.68, W 0.81 | W3A N 0.575x1.175 | 0% | yes |
| FF-05 | DINNING /LOUNGE | dining | 18.20 | 2.75 | N 2.68, E 0.79, S 1.68 | W3A N 0.575x1.175 | 23% | yes |
| FF-06 | ROOM | bedroom | 8.13 | 2.75 | N 3.01, E 2.6 | W1 E 1.2x1.54 | 0% | yes |
| FF-07 | KITCHEN | kitchen | 4.29 | 2.75 | S 1.63, W 2.6 | W1 W 1.2x1.54 | 0% | yes |
| FF-08 | BATH | bath | 1.58 | 2.75 | E 1.18 | - | 0% | no |
| FF-09 | WC | bath | 1.55 | 2.75 | N 0.85 | W1 N 1.2x1.54 | 0% | no |
| FF-10 | SHAFT | shaft | 2.67 | 2.75 | - | - | 27% | no |
| FF-11 | WC | bath | 1.55 | 2.75 | N 0.88 | W1 N 1.2x1.54 | 0% | no |
| FF-12 | BATH | bath | 1.62 | 2.75 | W 1.32 | - | 31% | no |
| FF-13 | KITCHEN | kitchen | 4.48 | 2.75 | E 2.6, S 1.63 | W1 E 1.2x1.54 | 0% | yes |
| FF-14 | ROOM | bedroom | 7.94 | 2.75 | W 2.6 | W3A W 0.575x1.175 | 12% | yes |
| FF-15 | ROOM | bedroom | 7.94 | 2.75 | E 2.59 | W3A E 0.575x1.175 | 16% | yes |
| FF-16 | ROOM | bedroom | 7.98 | 2.75 | W 2.61 | W3A W 0.575x1.175 | 16% | yes |
| FF-17 | ROOM | bedroom | 7.96 | 2.75 | E 2.6 | W3A E 0.575x1.175 | 22% | yes |
| FF-18 | KITCHEN | kitchen | 4.21 | 2.75 | N 1.64, W 2.58 | W4 N 0.575x1.175 | 63% | yes |
| FF-19 | BATH | bath | 1.57 | 2.75 | E 1.22 | - | 0% | no |
| FF-20 | WC | bath | 1.54 | 2.75 | S 0.89 | - | 0% | no |
| FF-21 | SHAFT | shaft | 2.63 | 2.75 | W 0.27 | W1 W 1.2x1.54 | 3% | no |
| FF-22 | WC | bath | 1.53 | 2.75 | S 0.77 | W1 S 1.2x1.54 | 44% | no |
| FF-23 | BATH | bath | 1.62 | 2.75 | W 1.3 | - | 0% | no |
| FF-24 | KITCHEN | kitchen | 4.21 | 2.75 | N 1.63, E 2.58 | W4 N 0.575x1.175, W1 E 1.2x1.54 | 63% | yes |
| FF-25 | ROOM | bedroom | 8.13 | 2.75 | S 2.71, W 2.6 | W1 W 1.2x1.54 | 0% | yes |
| FF-26 | DINNING /LOUNGE | dining | 18.01 | 2.75 | S 2.66, W 0.8, N 1.68 | W3A S 0.575x1.175, W3A N 0.575x1.175 | 22% | yes |
| FF-27 | DINNING /LOUNGE | dining | 18.14 | 2.75 | N 1.7, E 0.8, S 2.23 | W3A S 0.575x1.175, W3A N 0.575x1.175 | 16% | yes |
| FF-28 | ROOM | bedroom | 8.14 | 2.75 | E 2.6, S 2.84 | W1 E 1.2x1.54 | 0% | yes |
| FF-29 | TERRACE | outdoor | 5.98 | 2.75 | NW 0.09, W 2.29, S 3.01, E 0.81 | W3A NW 0.575x1.175 | 0% | no |
| FF-30 | TERRACE | outdoor | 6.38 | 2.75 | E 1.91, S 3.54, W 0.93 | W3A E 0.575x1.175 | 0% | no |
| SF-01 | TERRACE | outdoor | 7.69 | 2.75 | N 2.57, E 0.94, W 2.15 | W3A W 0.975x1.175 | 100% | no |
| SF-02 | TERRACE | outdoor | 8.26 | 2.75 | N 3.55, E 2.32, W 0.92 | W3A E 0.975x1.175 | 100% | no |
| SF-03 | ROOM | bedroom | 10.38 | 2.75 | N 3.39, W 2.94 | - | 4% | yes |
| SF-04 | ROOM | bedroom | 10.40 | 2.75 | N 3.38, E 1.23 | - | 4% | yes |
| SF-05 | KITCHEN | kitchen | 5.45 | 2.75 | S 1.85, W 2.93 | W4 S 0.975x1.175 | 0% | yes |
| SF-06 | DINNING /LOUNGE | dining | 23.07 | 2.75 | N 3.03, S 1.9, W 0.83 | W3A S 0.975x1.175 | 0% | yes |
| SF-07 | BATH | bath | 2.04 | 2.75 | E 1.35 | - | 0% | no |
| SF-08 | SHAFT | shaft | 3.37 | 2.75 | - | - | 7% | no |
| SF-09 | BATH | bath | 2.05 | 2.75 | W 1.32 | W1 W 0.575x0.875 | 0% | no |
| SF-10 | DINNING /LOUNGE | dining | 23.03 | 2.75 | N 3.03, E 1.02, S 1.9 | W3A N 0.975x1.175, W3A S 0.975x1.175 | 0% | yes |
| SF-11 | KITCHEN | kitchen | 5.74 | 2.75 | S 1.86 | - | 0% | yes |
| SF-12 | KITCHEN | kitchen | 4.90 | 2.75 | N 2.3, E 1.77, SE 1.25 | - | 100% | yes |
| SF-13 | WC | bath | 1.98 | 2.75 | N 1.04 | W1 N 0.575x0.875 | 0% | no |
| SF-14 | WC | bath | 1.98 | 2.75 | N 1.0 | - | 0% | no |
| SF-15 | ROOM | bedroom | 5.29 | 2.75 | E 3.16, W 1.05 | - | 100% | yes |
| SF-16 | ROOM | bedroom | 10.18 | 2.75 | W 2.94 | W3A W 0.975x1.175 | 0% | yes |
| SF-17 | ROOM | bedroom | 10.13 | 2.75 | E 2.93 | W3A E 0.975x1.175 | 0% | yes |
| SF-18 | OPEN TO SKY | outdoor | 13.03 | 2.75 | S 3.89 | - | 100% | no |
| SF-19 | ROOM | bedroom | 10.22 | 2.75 | W 2.95 | W3A W 0.975x1.175 | 0% | yes |
| SF-20 | WC | bath | 1.97 | 2.75 | S 1.01 | - | 0% | no |
| SF-21 | WC | bath | 1.96 | 2.75 | S 1.01 | - | 0% | no |
| SF-22 | ROOM | bedroom | 10.18 | 2.75 | E 2.94 | W3A E 0.975x1.175 | 0% | yes |
| SF-23 | KITCHEN | kitchen | 5.45 | 2.75 | N 1.84, W 2.93 | W4 N 0.975x1.175 | 4% | yes |
| SF-24 | DINNING /LOUNGE | dining | 23.06 | 2.75 | S 2.78, W 0.9, N 1.9 | W3A S 0.975x1.175 | 0% | yes |
| SF-25 | BATH | bath | 2.04 | 2.75 | E 1.43 | - | 0% | no |
| SF-26 | SHAFT | shaft | 3.65 | 2.75 | - | - | 0% | no |
| SF-27 | BATH | bath | 2.08 | 2.75 | W 1.49 | - | 0% | no |
| SF-28 | DINNING /LOUNGE | dining | 23.02 | 2.75 | N 1.9, E 1.06, S 3.03 | W3A S 0.975x1.175 | 0% | yes |
| SF-29 | KITCHEN | kitchen | 5.74 | 2.75 | N 1.86, E 2.93 | W4 N 0.975x1.175 | 3% | yes |
| SF-30 | ROOM | bedroom | 10.34 | 2.75 | S 2.88, W 2.93 | W1 W 0.575x0.875 | 0% | yes |
| SF-31 | ROOM | bedroom | 10.36 | 2.75 | E 2.93, S 2.77 | W1 E 0.575x0.875 | 0% | yes |
| SF-32 | TERRACE | outdoor | 7.53 | 2.75 | S 3.39, E 0.91, W 1.67 | W3A W 0.975x1.175 | 100% | no |
| SF-33 | TERRACE | outdoor | 8.04 | 2.75 | W 1.19, E 1.77, S 3.84 | W3A E 0.975x1.175 | 100% | no |
| SF-34 | BALCONY | outdoor | 2.33 | 2.75 | N 2.45, E 0.72, W 0.54 | - | 100% | no |
| SF-35 | BALCONY | outdoor | 2.74 | 2.75 | N 1.95, E 1.26, W 0.63 | W3A N 0.975x1.175 | 100% | no |
| SF-36 | BALCONY | outdoor | 2.65 | 2.75 | E 0.38, S 2.62, W 0.77 | - | 100% | no |
| SF-37 | BALCONY | outdoor | 2.83 | 2.75 | NE 0.16, W 0.68, E 0.97, S 3.02 | W3A NE 0.975x1.175 | 100% | no |
| TF-01 | TERRACE | outdoor | 8.30 | 2.75 | N 3.56, E 0.94, W 2.25 | - | 100% | no |
| TF-02 | BALCONY | outdoor | 2.33 | 2.75 | N 2.45, E 0.72, W 0.54 | - | 100% | no |
| TF-03 | BALCONY | outdoor | 2.74 | 2.75 | N 1.95, E 1.26, W 0.63 | W3A N 0.975x1.175 | 100% | no |
| TF-04 | TERRACE | outdoor | 8.72 | 2.75 | N 3.57, E 2.23, W 1.0 | W3A E 0.975x1.175 | 100% | no |
| TF-05 | ROOM | bedroom | 10.32 | 2.75 | N 3.43, W 2.95 | W3A N 0.975x1.175, W1 W 0.575x0.875 | 100% | yes |
| TF-06 | ROOM | bedroom | 10.36 | 2.75 | N 3.45, E 2.94 | W1 E 0.575x0.875 | 100% | yes |
| TF-07 | KITCHEN | kitchen | 5.45 | 2.75 | S 1.85, W 2.93 | W4 S 0.975x1.175 | 100% | yes |
| TF-08 | DINNING /LOUNGE | dining | 22.99 | 2.75 | N 1.38, S 1.9, W 0.95 | W3A N 0.975x1.175, W3A S 0.975x1.175 | 100% | yes |
| TF-09 | BATH | bath | 2.00 | 2.75 | E 1.33 | - | 100% | no |
| TF-10 | SHAFT | shaft | 3.37 | 2.75 | - | - | 100% | no |
| TF-11 | BATH | bath | 2.04 | 2.75 | W 1.4 | - | 100% | no |
| TF-12 | DINNING /LOUNGE | dining | 22.93 | 2.75 | N 2.86, E 0.93, S 1.9 | W3A S 0.975x1.175 | 100% | yes |
| TF-13 | KITCHEN | kitchen | 5.74 | 2.75 | E 2.93, S 1.86 | W4 S 0.975x1.175, W1 E 0.575x0.875 | 100% | yes |
| TF-14 | WC | bath | 1.98 | 2.75 | N 1.04 | W1 N 0.575x0.875 | 100% | no |
| TF-15 | WC | bath | 1.98 | 2.75 | N 1.0 | W1 N 0.575x0.875 | 100% | no |
| TF-16 | ROOM | bedroom | 10.13 | 2.75 | W 2.94 | W3A W 0.975x1.175 | 100% | yes |
| TF-17 | ROOM | bedroom | 10.13 | 2.75 | E 2.93 | W3A E 0.975x1.175 | 100% | yes |
| TF-18 | ROOM | bedroom | 10.18 | 2.75 | W 2.95 | W3A W 0.975x1.175 | 100% | yes |
| TF-19 | WC | bath | 1.97 | 2.75 | S 1.01 | - | 100% | no |
| TF-20 | WC | bath | 1.96 | 2.75 | S 1.01 | - | 100% | no |
| TF-21 | ROOM | bedroom | 10.18 | 2.75 | E 2.94 | W3A E 0.975x1.175 | 100% | yes |
| TF-22 | KITCHEN | kitchen | 5.45 | 2.75 | N 1.85, W 2.93 | W4 N 0.975x1.175 | 100% | yes |
| TF-23 | DINNING /LOUNGE | dining | 22.98 | 2.75 | S 2.18, W 0.96, N 1.9 | W3A S 0.975x1.175 | 100% | yes |
| TF-24 | BATH | bath | 2.01 | 2.75 | E 1.37 | - | 100% | no |
| TF-25 | SHAFT | shaft | 3.65 | 2.75 | - | - | 100% | no |
| TF-26 | BATH | bath | 2.08 | 2.75 | W 1.48 | - | 100% | no |
| TF-27 | DINNING /LOUNGE | dining | 22.92 | 2.75 | N 1.9, E 0.96, S 2.5 | - | 100% | yes |
| TF-28 | KITCHEN | kitchen | 5.74 | 2.75 | N 1.86, E 2.93 | W4 N 0.975x1.175, W1 E 0.575x0.875 | 100% | yes |
| TF-29 | ROOM | bedroom | 10.29 | 2.75 | S 3.45, W 2.93 | W3A S 0.975x1.175, W1 W 0.575x0.875 | 100% | yes |
| TF-30 | ROOM | bedroom | 10.32 | 2.75 | E 2.93, S 3.46 | W3A S 0.975x1.175, W1 E 0.575x0.875 | 100% | yes |
| TF-31 | TERRACE | outdoor | 8.35 | 2.75 | E 0.95, S 3.57, W 2.27 | - | 100% | no |
| TF-32 | BALCONY | outdoor | 2.65 | 2.75 | E 0.38, S 2.62, W 0.77 | - | 100% | no |
| TF-33 | BALCONY | outdoor | 2.83 | 2.75 | NE 0.16, W 0.68, E 0.97, S 3.02 | W3A NE 0.975x1.175 | 100% | no |
| TF-34 | TERRACE | outdoor | 8.80 | 2.75 | E 2.37, S 3.59, W 1.01 | - | 100% | no |

# 3. Cooling and heating loads

Method: CLTD/SCL/CLF (ASHRAE Fundamentals 1997 Ch.28). Conduction Q = U·A·CLTDc with CLTDc = (CLTD + LM)·K + (25.5 − Ti) + (Tm − 29.4), Tm = To − DR/2. Glass solar Q = A·SC·SHGF·CLF. People/lights/equipment with CLF = 1.0. Infiltration Qs = Cs·V·ΔT, Ql = Cl·V·ΔW. Loads are computed for solar hours 8-20; each room is sized at its own peak, zones and plant at the coincident (block) peak. Heating: Q = ΣU·A·(Ti − To,w) + infiltration + slab edge, no internal gains.

Code reference: ASHRAE Fundamentals 1997 Ch.28 CLTD/SCL/CLF method, Tables 30-36; ASHRAE Fundamentals 2021 Ch.16 §'Residential air change method'

| ID | Room | m² | Walls | Roof | Glass cond. | Glass solar | People S | Lights | Equip S | Infil S | Sensible W | Latent W | Total W | W/m² | Peak | Supply | Heating W |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| GF-02 | ROOM | 8.12 | 55.0 | 19.0 | 33.0 | 21.0 | 120.0 | 65.0 | 41.0 | 77.0 | 429 | 50 | 479 | 59.0 | 15:00 | 34 L/s | 187 |
| GF-03 | ROOM | 8.13 | 64.0 | 21.0 | 0.0 | 0.0 | 120.0 | 65.0 | 41.0 | 72.0 | 381 | 50 | 431 | 53.1 | 17:00 | 30 L/s | 164 |
| GF-11 | ROOM | 8.05 | 55.0 | 0.0 | 23.0 | 95.0 | 120.0 | 64.0 | 40.0 | 47.0 | 445 | 50 | 495 | 61.4 | 10:00 | 35 L/s | 165 |
| GF-14 | ROOM | 7.57 | 70.0 | 0.0 | 31.0 | 104.0 | 120.0 | 61.0 | 38.0 | 61.0 | 485 | 50 | 535 | 70.7 | 18:00 | 39 L/s | 162 |
| GF-15 | ROOM | 8.07 | 55.0 | 0.0 | 23.0 | 95.0 | 120.0 | 65.0 | 40.0 | 47.0 | 445 | 50 | 495 | 61.3 | 10:00 | 35 L/s | 165 |
| GF-24 | ROOM | 8.12 | 59.0 | 0.0 | 0.0 | 0.0 | 120.0 | 65.0 | 41.0 | 75.0 | 360 | 50 | 410 | 50.5 | 16:00 | 29 L/s | 155 |
| GF-25 | DINNING /LOUNGE | 18.44 | 85.0 | 12.0 | 66.0 | 39.0 | 560.0 | 184.0 | 55.0 | 261.0 | 1262 | 360 | 1622 | 87.9 | 15:00 | 100 L/s | 394 |
| GF-26 | DINNING /LOUNGE | 18.4 | 147.0 | 13.0 | 66.0 | 38.0 | 560.0 | 184.0 | 55.0 | 255.0 | 1317 | 360 | 1677 | 91.2 | 16:00 | 105 L/s | 473 |
| GF-27 | ROOM | 8.13 | 54.0 | 0.0 | 33.0 | 19.0 | 120.0 | 65.0 | 41.0 | 75.0 | 407 | 50 | 457 | 56.2 | 16:00 | 32 L/s | 177 |
| GF-31 | DINNING /LOUNGE | 18.13 | 95.0 | 0.0 | 33.0 | 21.0 | 560.0 | 181.0 | 54.0 | 257.0 | 1201 | 360 | 1561 | 86.1 | 15:00 | 96 L/s | 282 |
| GF-32 | DINNING /LOUNGE | 18.2 | 102.0 | 24.0 | 33.0 | 21.0 | 560.0 | 182.0 | 55.0 | 258.0 | 1233 | 360 | 1593 | 87.5 | 15:00 | 98 L/s | 295 |
| GF-38 | ROOM | 7.94 | 68.0 | 6.0 | 31.0 | 104.0 | 120.0 | 64.0 | 40.0 | 64.0 | 496 | 50 | 546 | 68.8 | 18:00 | 40 L/s | 120 |
| FF-03 | ROOM | 8.11 | 122.0 | 3.0 | 84.0 | 286.0 | 120.0 | 65.0 | 41.0 | 98.0 | 819 | 50 | 869 | 107.1 | 18:00 | 65 L/s | 235 |
| FF-04 | DINNING /LOUNGE | 18.13 | 95.0 | 0.0 | 33.0 | 21.0 | 560.0 | 181.0 | 54.0 | 257.0 | 1201 | 360 | 1561 | 86.1 | 15:00 | 96 L/s | 282 |
| FF-05 | DINNING /LOUNGE | 18.2 | 102.0 | 24.0 | 33.0 | 21.0 | 560.0 | 182.0 | 55.0 | 258.0 | 1233 | 360 | 1593 | 87.5 | 15:00 | 98 L/s | 295 |
| FF-06 | ROOM | 8.13 | 91.0 | 0.0 | 57.0 | 293.0 | 120.0 | 65.0 | 41.0 | 60.0 | 726 | 50 | 776 | 95.5 | 9:00 | 58 L/s | 234 |
| FF-14 | ROOM | 7.94 | 68.0 | 6.0 | 31.0 | 104.0 | 120.0 | 64.0 | 40.0 | 64.0 | 496 | 50 | 546 | 68.8 | 18:00 | 40 L/s | 120 |
| FF-15 | ROOM | 7.94 | 53.0 | 4.0 | 23.0 | 95.0 | 120.0 | 64.0 | 40.0 | 47.0 | 445 | 50 | 495 | 62.3 | 10:00 | 35 L/s | 121 |
| FF-16 | ROOM | 7.98 | 68.0 | 8.0 | 31.0 | 104.0 | 120.0 | 64.0 | 40.0 | 65.0 | 500 | 50 | 550 | 68.9 | 18:00 | 40 L/s | 121 |
| FF-17 | ROOM | 7.96 | 53.0 | 6.0 | 23.0 | 95.0 | 120.0 | 64.0 | 40.0 | 47.0 | 447 | 50 | 497 | 62.4 | 10:00 | 36 L/s | 122 |
| FF-25 | ROOM | 8.13 | 113.0 | 0.0 | 84.0 | 286.0 | 120.0 | 65.0 | 41.0 | 99.0 | 807 | 50 | 857 | 105.5 | 18:00 | 64 L/s | 229 |
| FF-26 | DINNING /LOUNGE | 18.01 | 95.0 | 24.0 | 66.0 | 38.0 | 560.0 | 180.0 | 54.0 | 250.0 | 1266 | 360 | 1626 | 90.3 | 16:00 | 101 L/s | 315 |
| FF-27 | DINNING /LOUNGE | 18.14 | 89.0 | 17.0 | 66.0 | 39.0 | 560.0 | 181.0 | 54.0 | 257.0 | 1262 | 360 | 1622 | 89.4 | 15:00 | 100 L/s | 306 |
| FF-28 | ROOM | 8.14 | 71.0 | 0.0 | 57.0 | 293.0 | 120.0 | 65.0 | 41.0 | 60.0 | 707 | 50 | 757 | 92.9 | 9:00 | 56 L/s | 231 |
| SF-03 | ROOM | 10.38 | 158.0 | 3.0 | 0.0 | 0.0 | 120.0 | 83.0 | 52.0 | 126.0 | 542 | 50 | 592 | 57.0 | 18:00 | 43 L/s | 208 |
| SF-04 | ROOM | 10.4 | 101.0 | 2.0 | 0.0 | 0.0 | 120.0 | 83.0 | 52.0 | 147.0 | 506 | 50 | 556 | 53.4 | 15:00 | 40 L/s | 179 |
| SF-06 | DINNING /LOUNGE | 23.07 | 110.0 | 0.0 | 56.0 | 32.0 | 700.0 | 231.0 | 69.0 | 320.0 | 1517 | 450 | 1967 | 85.3 | 16:00 | 121 L/s | 355 |
| SF-10 | DINNING /LOUNGE | 23.03 | 109.0 | 0.0 | 111.0 | 66.0 | 700.0 | 230.0 | 69.0 | 326.0 | 1611 | 450 | 2061 | 89.5 | 15:00 | 128 L/s | 395 |
| SF-15 | ROOM | 5.29 | 112.0 | 32.0 | 0.0 | 0.0 | 120.0 | 42.0 | 26.0 | 73.0 | 406 | 50 | 456 | 86.2 | 16:00 | 32 L/s | 138 |
| SF-16 | ROOM | 10.18 | 73.0 | 0.0 | 52.0 | 177.0 | 120.0 | 81.0 | 51.0 | 82.0 | 637 | 50 | 687 | 67.5 | 18:00 | 51 L/s | 152 |
| SF-17 | ROOM | 10.13 | 52.0 | 0.0 | 35.0 | 182.0 | 120.0 | 81.0 | 51.0 | 50.0 | 570 | 50 | 620 | 61.2 | 9:00 | 45 L/s | 152 |
| SF-19 | ROOM | 10.22 | 73.0 | 0.0 | 52.0 | 177.0 | 120.0 | 82.0 | 51.0 | 83.0 | 638 | 50 | 688 | 67.3 | 18:00 | 51 L/s | 153 |
| SF-22 | ROOM | 10.18 | 52.0 | 0.0 | 35.0 | 182.0 | 120.0 | 81.0 | 51.0 | 50.0 | 571 | 50 | 621 | 61.0 | 9:00 | 45 L/s | 152 |
| SF-24 | DINNING /LOUNGE | 23.06 | 106.0 | 0.0 | 56.0 | 32.0 | 700.0 | 231.0 | 69.0 | 320.0 | 1513 | 450 | 1963 | 85.1 | 16:00 | 120 L/s | 352 |
| SF-28 | DINNING /LOUNGE | 23.02 | 116.0 | 0.0 | 56.0 | 31.0 | 700.0 | 230.0 | 69.0 | 326.0 | 1528 | 450 | 1978 | 85.9 | 15:00 | 122 L/s | 358 |
| SF-30 | ROOM | 10.34 | 139.0 | 0.0 | 23.0 | 78.0 | 120.0 | 83.0 | 52.0 | 126.0 | 619 | 50 | 669 | 64.7 | 18:00 | 49 L/s | 214 |
| SF-31 | ROOM | 10.36 | 129.0 | 0.0 | 24.0 | 22.0 | 120.0 | 83.0 | 52.0 | 147.0 | 576 | 50 | 626 | 60.5 | 15:00 | 46 L/s | 213 |
| TF-05 | ROOM | 10.32 | 146.0 | 64.0 | 75.0 | 117.0 | 120.0 | 83.0 | 52.0 | 125.0 | 781 | 50 | 831 | 80.6 | 18:00 | 62 L/s | 291 |
| TF-06 | ROOM | 10.36 | 147.0 | 63.0 | 24.0 | 20.0 | 120.0 | 83.0 | 52.0 | 144.0 | 653 | 50 | 703 | 67.9 | 16:00 | 52 L/s | 254 |
| TF-08 | DINNING /LOUNGE | 22.99 | 71.0 | 140.0 | 111.0 | 64.0 | 700.0 | 230.0 | 69.0 | 319.0 | 1704 | 450 | 2154 | 93.7 | 16:00 | 136 L/s | 431 |
| TF-12 | DINNING /LOUNGE | 22.93 | 114.0 | 139.0 | 56.0 | 32.0 | 700.0 | 229.0 | 69.0 | 318.0 | 1657 | 450 | 2107 | 91.9 | 16:00 | 132 L/s | 418 |
| TF-16 | ROOM | 10.13 | 73.0 | 63.0 | 52.0 | 177.0 | 120.0 | 81.0 | 51.0 | 82.0 | 699 | 50 | 749 | 73.9 | 18:00 | 56 L/s | 181 |
| TF-17 | ROOM | 10.13 | 57.0 | 32.0 | 39.0 | 161.0 | 120.0 | 81.0 | 51.0 | 59.0 | 600 | 50 | 650 | 64.2 | 10:00 | 48 L/s | 181 |
| TF-18 | ROOM | 10.18 | 73.0 | 63.0 | 52.0 | 177.0 | 120.0 | 81.0 | 51.0 | 82.0 | 700 | 50 | 750 | 73.7 | 18:00 | 56 L/s | 182 |
| TF-21 | ROOM | 10.18 | 57.0 | 32.0 | 39.0 | 161.0 | 120.0 | 81.0 | 51.0 | 60.0 | 602 | 50 | 652 | 64.0 | 10:00 | 48 L/s | 182 |
| TF-23 | DINNING /LOUNGE | 22.98 | 95.0 | 140.0 | 56.0 | 32.0 | 700.0 | 230.0 | 69.0 | 319.0 | 1640 | 450 | 2090 | 90.9 | 16:00 | 130 L/s | 408 |
| TF-27 | DINNING /LOUNGE | 22.92 | 114.0 | 139.0 | 0.0 | 0.0 | 700.0 | 229.0 | 69.0 | 318.0 | 1569 | 450 | 2019 | 88.1 | 16:00 | 125 L/s | 375 |
| TF-29 | ROOM | 10.29 | 133.0 | 64.0 | 78.0 | 101.0 | 120.0 | 82.0 | 51.0 | 136.0 | 765 | 50 | 815 | 79.2 | 17:00 | 61 L/s | 291 |
| TF-30 | ROOM | 10.32 | 138.0 | 63.0 | 80.0 | 52.0 | 120.0 | 83.0 | 52.0 | 143.0 | 730 | 50 | 780 | 75.5 | 16:00 | 58 L/s | 291 |

Conditioned area 627.5 m²; sum of room peaks 49.8 kW; block peak 48.9 kW at 17:00 (78 W/m²); heating 11.9 kW. Safety factors are applied at equipment selection (section 5).

## 3.1 Worked example - TF-08 DINNING /LOUNGE at 16:00

| Item | Calculation |
| --- | --- |
| Wall N | U 0.4 × A 2.99 m² (gross 4.14) |
| Wall S | U 0.4 × A 4.55 m² (gross 5.7) |
| Wall W | U 0.4 × A 2.85 m² (gross 2.85) |
| Window W3A N | cond. U 2.67 × 1.15 m²; solar 1.15 × SC 0.287 × SHGF 130 × CLF |
| Window W3A S | cond. U 2.67 × 1.15 m²; solar 1.15 × SC 0.287 × SHGF 110 × CLF |
| Roof | U 0.2 × 22.99 m² |
| People | 10 persons |
| Infiltration | 0.75 ACH × 63.2 m³ = 13.2 L/s |
| wall | 71.0 W |
| roof | 140.0 W |
| glass_cond | 111.0 W |
| glass_solar | 64.0 W |
| people_s | 700.0 W |
| lights | 230.0 W |
| equip_s | 69.0 W |
| infil_s | 319.0 W |
| people_l | 450 W |
| equip_l | 0 W |
| infil_l | 0 W |
| Room sensible / latent / total | 1704 / 450 / 2154 W |
| Supply airflow | 1704 W / (1.143 × (24.0 − 13.0)) = 135.5 L/s |

# 4. Ventilation and exhaust

Ventilation rate procedure: Vbz = Rp·Pz + Ra·Az; Voz = Vbz / Ez; single-zone Vot = Voz; multiple-zone Vot = (D·ΣRp·Pz + ΣRa·Az)/Ev.

Code reference: SBC 501 §403.3.1.1 & Table 403.3.1.1; ASHRAE 62.1-2019 §6.2.2.1 Eq.6-1, Table 6-1; ASHRAE 62.1-2019 §6.2.2.2 Table 6-2 (Ez); ASHRAE 62.1-2019 §6.2.4.3.1 simplified procedure (Ev)

| Zone | Room | Category | Pz | Az m² | Rp·Pz | Ra·Az | Vbz L/s | Ez | Ev | Zone Vot L/s | OA method |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Z-GF-01 | GF-02 | dwelling | 2 | 8.12 | 5.0 | 2.4 | 7.4 | 0.8 | 1.0 | 9.3 | through-wall fresh air fan |
| Z-GF-02 | GF-03 | dwelling | 2 | 8.13 | 5.0 | 2.4 | 7.4 | 0.8 | 1.0 | 9.3 | through-wall fresh air fan |
| Z-GF-03 | GF-11 | dwelling | 2 | 8.05 | 5.0 | 2.4 | 7.4 | 0.8 | 1.0 | 9.3 | through-wall fresh air fan |
| Z-GF-04 | GF-14 | dwelling | 2 | 7.57 | 5.0 | 2.3 | 7.3 | 0.8 | 1.0 | 9.1 | through-wall fresh air fan |
| Z-GF-05 | GF-15 | dwelling | 2 | 8.07 | 5.0 | 2.4 | 7.4 | 0.8 | 1.0 | 9.3 | through-wall fresh air fan |
| Z-GF-06 | GF-24 | dwelling | 2 | 8.12 | 5.0 | 2.4 | 7.4 | 0.8 | 1.0 | 9.3 | through-wall fresh air fan |
| Z-GF-07 | GF-27 | dwelling | 2 | 8.13 | 5.0 | 2.4 | 7.4 | 0.8 | 1.0 | 9.3 | through-wall fresh air fan |
| Z-GF-08 | GF-38 | dwelling | 2 | 7.94 | 5.0 | 2.4 | 7.4 | 0.8 | 1.0 | 9.2 | through-wall fresh air fan |
| Z-GF-09 | GF-25 | dwelling | 8 | 18.44 | 20.0 | 5.5 | 25.5 | 0.8 | 1.0 | 31.9 | ducted to unit return plenum |
| Z-GF-10 | GF-26 | dwelling | 8 | 18.4 | 20.0 | 5.5 | 25.5 | 0.8 | 1.0 | 31.9 | ducted to unit return plenum |
| Z-GF-11 | GF-31 | dwelling | 8 | 18.13 | 20.0 | 5.4 | 25.4 | 0.8 | 1.0 | 31.8 | ducted to unit return plenum |
| Z-GF-12 | GF-32 | dwelling | 8 | 18.2 | 20.0 | 5.5 | 25.5 | 0.8 | 1.0 | 31.8 | ducted to unit return plenum |
| Z-FF-01 | FF-03 | dwelling | 2 | 8.11 | 5.0 | 2.4 | 7.4 | 0.8 | 1.0 | 9.3 | through-wall fresh air fan |
| Z-FF-02 | FF-06 | dwelling | 2 | 8.13 | 5.0 | 2.4 | 7.4 | 0.8 | 1.0 | 9.3 | through-wall fresh air fan |
| Z-FF-03 | FF-14 | dwelling | 2 | 7.94 | 5.0 | 2.4 | 7.4 | 0.8 | 1.0 | 9.2 | through-wall fresh air fan |
| Z-FF-04 | FF-15 | dwelling | 2 | 7.94 | 5.0 | 2.4 | 7.4 | 0.8 | 1.0 | 9.2 | through-wall fresh air fan |
| Z-FF-05 | FF-16 | dwelling | 2 | 7.98 | 5.0 | 2.4 | 7.4 | 0.8 | 1.0 | 9.2 | through-wall fresh air fan |
| Z-FF-06 | FF-17 | dwelling | 2 | 7.96 | 5.0 | 2.4 | 7.4 | 0.8 | 1.0 | 9.2 | through-wall fresh air fan |
| Z-FF-07 | FF-25 | dwelling | 2 | 8.13 | 5.0 | 2.4 | 7.4 | 0.8 | 1.0 | 9.3 | through-wall fresh air fan |
| Z-FF-08 | FF-28 | dwelling | 2 | 8.14 | 5.0 | 2.4 | 7.4 | 0.8 | 1.0 | 9.3 | through-wall fresh air fan |
| Z-FF-09 | FF-04 | dwelling | 8 | 18.13 | 20.0 | 5.4 | 25.4 | 0.8 | 1.0 | 31.8 | ducted to unit return plenum |
| Z-FF-10 | FF-05 | dwelling | 8 | 18.2 | 20.0 | 5.5 | 25.5 | 0.8 | 1.0 | 31.8 | ducted to unit return plenum |
| Z-FF-11 | FF-26 | dwelling | 8 | 18.01 | 20.0 | 5.4 | 25.4 | 0.8 | 1.0 | 31.8 | ducted to unit return plenum |
| Z-FF-12 | FF-27 | dwelling | 8 | 18.14 | 20.0 | 5.4 | 25.4 | 0.8 | 1.0 | 31.8 | ducted to unit return plenum |
| Z-SF-01 | SF-03 | dwelling | 2 | 10.38 | 5.0 | 3.1 | 8.1 | 0.8 | 1.0 | 10.1 | through-wall fresh air fan |
| Z-SF-02 | SF-04 | dwelling | 2 | 10.4 | 5.0 | 3.1 | 8.1 | 0.8 | 1.0 | 10.2 | through-wall fresh air fan |
| Z-SF-03 | SF-15 | dwelling | 2 | 5.29 | 5.0 | 1.6 | 6.6 | 0.8 | 1.0 | 8.2 | through-wall fresh air fan |
| Z-SF-04 | SF-16 | dwelling | 2 | 10.18 | 5.0 | 3.1 | 8.1 | 0.8 | 1.0 | 10.1 | through-wall fresh air fan |
| Z-SF-05 | SF-17 | dwelling | 2 | 10.13 | 5.0 | 3.0 | 8.0 | 0.8 | 1.0 | 10.0 | through-wall fresh air fan |
| Z-SF-06 | SF-19 | dwelling | 2 | 10.22 | 5.0 | 3.1 | 8.1 | 0.8 | 1.0 | 10.1 | through-wall fresh air fan |
| Z-SF-07 | SF-22 | dwelling | 2 | 10.18 | 5.0 | 3.1 | 8.1 | 0.8 | 1.0 | 10.1 | through-wall fresh air fan |
| Z-SF-08 | SF-30 | dwelling | 2 | 10.34 | 5.0 | 3.1 | 8.1 | 0.8 | 1.0 | 10.1 | through-wall fresh air fan |
| Z-SF-09 | SF-31 | dwelling | 2 | 10.36 | 5.0 | 3.1 | 8.1 | 0.8 | 1.0 | 10.1 | through-wall fresh air fan |
| Z-SF-10 | SF-06 | dwelling | 10 | 23.07 | 25.0 | 6.9 | 31.9 | 0.8 | 1.0 | 39.9 | ducted to unit return plenum |
| Z-SF-11 | SF-10 | dwelling | 10 | 23.03 | 25.0 | 6.9 | 31.9 | 0.8 | 1.0 | 39.9 | ducted to unit return plenum |
| Z-SF-12 | SF-24 | dwelling | 10 | 23.06 | 25.0 | 6.9 | 31.9 | 0.8 | 1.0 | 39.9 | ducted to unit return plenum |
| Z-SF-13 | SF-28 | dwelling | 10 | 23.02 | 25.0 | 6.9 | 31.9 | 0.8 | 1.0 | 39.9 | ducted to unit return plenum |
| Z-TF-01 | TF-05 | dwelling | 2 | 10.32 | 5.0 | 3.1 | 8.1 | 0.8 | 1.0 | 10.1 | through-wall fresh air fan |
| Z-TF-02 | TF-06 | dwelling | 2 | 10.36 | 5.0 | 3.1 | 8.1 | 0.8 | 1.0 | 10.1 | through-wall fresh air fan |
| Z-TF-03 | TF-16 | dwelling | 2 | 10.13 | 5.0 | 3.0 | 8.0 | 0.8 | 1.0 | 10.0 | through-wall fresh air fan |
| Z-TF-04 | TF-17 | dwelling | 2 | 10.13 | 5.0 | 3.0 | 8.0 | 0.8 | 1.0 | 10.0 | through-wall fresh air fan |
| Z-TF-05 | TF-18 | dwelling | 2 | 10.18 | 5.0 | 3.1 | 8.1 | 0.8 | 1.0 | 10.1 | through-wall fresh air fan |
| Z-TF-06 | TF-21 | dwelling | 2 | 10.18 | 5.0 | 3.1 | 8.1 | 0.8 | 1.0 | 10.1 | through-wall fresh air fan |
| Z-TF-07 | TF-29 | dwelling | 2 | 10.29 | 5.0 | 3.1 | 8.1 | 0.8 | 1.0 | 10.1 | through-wall fresh air fan |
| Z-TF-08 | TF-30 | dwelling | 2 | 10.32 | 5.0 | 3.1 | 8.1 | 0.8 | 1.0 | 10.1 | through-wall fresh air fan |
| Z-TF-09 | TF-08 | dwelling | 10 | 22.99 | 25.0 | 6.9 | 31.9 | 0.8 | 1.0 | 39.9 | ducted to unit return plenum |
| Z-TF-10 | TF-12 | dwelling | 10 | 22.93 | 25.0 | 6.9 | 31.9 | 0.8 | 1.0 | 39.8 | ducted to unit return plenum |
| Z-TF-11 | TF-23 | dwelling | 10 | 22.98 | 25.0 | 6.9 | 31.9 | 0.8 | 1.0 | 39.9 | ducted to unit return plenum |
| Z-TF-12 | TF-27 | dwelling | 10 | 22.92 | 25.0 | 6.9 | 31.9 | 0.8 | 1.0 | 39.8 | ducted to unit return plenum |

| Room | Name | Rule | Exhaust L/s | Mode | Clause |
| --- | --- | --- | --- | --- | --- |
| GF-04 | KITCHEN | kitchen_residential | 50.0 | intermittent | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| GF-05 | BATH | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| GF-06 | WC | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| GF-08 | WC | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| GF-09 | BATH | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| GF-17 | KITCHEN | kitchen_residential | 50.0 | intermittent | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| GF-18 | BATH | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| GF-19 | WC | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| GF-21 | WC | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| GF-22 | BATH | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| GF-23 | KITCHEN | kitchen_residential | 50.0 | intermittent | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| GF-33 | BATH | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| GF-34 | WC | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| GF-36 | BATH | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| GF-37 | KITCHEN | kitchen_residential | 50.0 | intermittent | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| FF-07 | KITCHEN | kitchen_residential | 50.0 | intermittent | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| FF-08 | BATH | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| FF-09 | WC | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| FF-11 | WC | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| FF-12 | BATH | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| FF-13 | KITCHEN | kitchen_residential | 50.0 | intermittent | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| FF-18 | KITCHEN | kitchen_residential | 50.0 | intermittent | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| FF-19 | BATH | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| FF-20 | WC | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| FF-22 | WC | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| FF-23 | BATH | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| FF-24 | KITCHEN | kitchen_residential | 50.0 | intermittent | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| SF-05 | KITCHEN | kitchen_residential | 50.0 | intermittent | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| SF-07 | BATH | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| SF-09 | BATH | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| SF-11 | KITCHEN | kitchen_residential | 50.0 | intermittent | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| SF-12 | KITCHEN | kitchen_residential | 50.0 | intermittent | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| SF-13 | WC | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| SF-14 | WC | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| SF-20 | WC | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| SF-21 | WC | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| SF-23 | KITCHEN | kitchen_residential | 50.0 | intermittent | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| SF-25 | BATH | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| SF-27 | BATH | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| SF-29 | KITCHEN | kitchen_residential | 50.0 | intermittent | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| TF-07 | KITCHEN | kitchen_residential | 50.0 | intermittent | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| TF-09 | BATH | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| TF-11 | BATH | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| TF-13 | KITCHEN | kitchen_residential | 50.0 | intermittent | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| TF-14 | WC | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| TF-15 | WC | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| TF-19 | WC | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| TF-20 | WC | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| TF-22 | KITCHEN | kitchen_residential | 50.0 | intermittent | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| TF-24 | BATH | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| TF-26 | BATH | toilet_private | 25.0 | intermittent | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| TF-28 | KITCHEN | kitchen_residential | 50.0 | intermittent | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |

Building outdoor air 891 L/s; exhaust 1,725 L/s (net -834 L/s). ASHRAE 62.2 whole-house cross-check: 213 L/s - design OA exceeds it.

# 5. Zoning and equipment selection

Required capacity = coincident zone load (rooms + outdoor air) × (1 + SF), SF cooling 10%, heating 10%. Nominal capacities × 0.88 for high-ambient (T3) operation. Selection = smallest catalogue unit meeting total, sensible and airflow.

Code reference: Designer allowance - not a code requirement; SASO 2663 / SBC 601 Table C403.3.2 minimum efficiency

| Zone | Rooms | System | Peak h | Rooms kW | OA kW | Block kW | SF | Req. kW | Req. sens kW | Req. air | Selected | Derated kW | Sens kW | Unit air | OA % | Input kW | Heat kW sel/req |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Z-GF-01 | GF-02 | wall_split | 15 | 0.48 | 0.23 | 0.71 | 10% | 0.78 | 0.72 | 34 L/s | IU-GF-01 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.37 |
| Z-GF-02 | GF-03 | wall_split | 15 | 0.43 | 0.23 | 0.66 | 10% | 0.73 | 0.67 | 30 L/s | IU-GF-02 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.35 |
| Z-GF-03 | GF-11 | wall_split | 15 | 0.48 | 0.23 | 0.71 | 10% | 0.78 | 0.73 | 35 L/s | IU-GF-03 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.35 |
| Z-GF-04 | GF-14 | wall_split | 17 | 0.52 | 0.21 | 0.73 | 10% | 0.81 | 0.75 | 39 L/s | IU-GF-04 WS-09 | 2.29 | 1.74 | 140 L/s | 6% | 0.76 | 2.9 / 0.34 |
| Z-GF-05 | GF-15 | wall_split | 15 | 0.48 | 0.23 | 0.71 | 10% | 0.78 | 0.73 | 35 L/s | IU-GF-05 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.35 |
| Z-GF-06 | GF-24 | wall_split | 15 | 0.41 | 0.23 | 0.64 | 10% | 0.7 | 0.65 | 30 L/s | IU-GF-06 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.34 |
| Z-GF-07 | GF-27 | wall_split | 15 | 0.46 | 0.23 | 0.68 | 10% | 0.75 | 0.7 | 32 L/s | IU-GF-07 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.36 |
| Z-GF-08 | GF-38 | wall_split | 17 | 0.54 | 0.21 | 0.75 | 10% | 0.82 | 0.77 | 40 L/s | IU-GF-08 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.3 |
| Z-GF-09 | GF-25 | ducted_split | 15 | 1.62 | 0.79 | 2.41 | 10% | 2.65 | 2.25 | 100 L/s | IU-GF-09 DS-18 | 4.66 | 3.5 | 300 L/s | 11% | 1.66 | 5.8 / 1.01 |
| Z-GF-10 | GF-26 | ducted_split | 15 | 1.67 | 0.79 | 2.46 | 10% | 2.71 | 2.31 | 105 L/s | IU-GF-10 DS-18 | 4.66 | 3.5 | 300 L/s | 11% | 1.66 | 5.8 / 1.1 |
| Z-GF-11 | GF-31 | ducted_split | 15 | 1.56 | 0.79 | 2.35 | 10% | 2.58 | 2.18 | 96 L/s | IU-GF-11 DS-18 | 4.66 | 3.5 | 300 L/s | 11% | 1.66 | 5.8 / 0.89 |
| Z-GF-12 | GF-32 | ducted_split | 15 | 1.59 | 0.79 | 2.38 | 10% | 2.62 | 2.22 | 98 L/s | IU-GF-12 DS-18 | 4.66 | 3.5 | 300 L/s | 11% | 1.66 | 5.8 / 0.9 |
| Z-FF-01 | FF-03 | wall_split | 18 | 0.87 | 0.2 | 1.07 | 10% | 1.17 | 1.12 | 65 L/s | IU-FF-01 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.43 |
| Z-FF-02 | FF-06 | wall_split | 10 | 0.77 | 0.14 | 0.91 | 10% | 1.0 | 0.95 | 58 L/s | IU-FF-02 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.43 |
| Z-FF-03 | FF-14 | wall_split | 17 | 0.54 | 0.21 | 0.75 | 10% | 0.82 | 0.77 | 40 L/s | IU-FF-03 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.3 |
| Z-FF-04 | FF-15 | wall_split | 15 | 0.48 | 0.23 | 0.71 | 10% | 0.78 | 0.73 | 35 L/s | IU-FF-04 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.3 |
| Z-FF-05 | FF-16 | wall_split | 17 | 0.54 | 0.21 | 0.75 | 10% | 0.83 | 0.77 | 40 L/s | IU-FF-05 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.3 |
| Z-FF-06 | FF-17 | wall_split | 15 | 0.49 | 0.23 | 0.71 | 10% | 0.79 | 0.73 | 36 L/s | IU-FF-06 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.3 |
| Z-FF-07 | FF-25 | wall_split | 18 | 0.86 | 0.2 | 1.05 | 10% | 1.16 | 1.1 | 64 L/s | IU-FF-07 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.42 |
| Z-FF-08 | FF-28 | wall_split | 15 | 0.67 | 0.23 | 0.9 | 10% | 0.99 | 0.93 | 56 L/s | IU-FF-08 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.42 |
| Z-FF-09 | FF-04 | ducted_split | 15 | 1.56 | 0.79 | 2.35 | 10% | 2.58 | 2.18 | 96 L/s | IU-FF-09 DS-18 | 4.66 | 3.5 | 300 L/s | 11% | 1.66 | 5.8 / 0.89 |
| Z-FF-10 | FF-05 | ducted_split | 15 | 1.59 | 0.79 | 2.38 | 10% | 2.62 | 2.22 | 98 L/s | IU-FF-10 DS-18 | 4.66 | 3.5 | 300 L/s | 11% | 1.66 | 5.8 / 0.9 |
| Z-FF-11 | FF-26 | ducted_split | 15 | 1.63 | 0.79 | 2.41 | 10% | 2.65 | 2.26 | 101 L/s | IU-FF-11 DS-18 | 4.66 | 3.5 | 300 L/s | 11% | 1.66 | 5.8 / 0.92 |
| Z-FF-12 | FF-27 | ducted_split | 15 | 1.62 | 0.79 | 2.41 | 10% | 2.65 | 2.25 | 100 L/s | IU-FF-12 DS-18 | 4.66 | 3.5 | 300 L/s | 11% | 1.66 | 5.8 / 0.91 |
| Z-SF-01 | SF-03 | wall_split | 16 | 0.59 | 0.24 | 0.83 | 10% | 0.91 | 0.86 | 43 L/s | IU-SF-01 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.41 |
| Z-SF-02 | SF-04 | wall_split | 15 | 0.56 | 0.25 | 0.81 | 10% | 0.89 | 0.83 | 40 L/s | IU-SF-02 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.38 |
| Z-SF-03 | SF-15 | wall_split | 15 | 0.45 | 0.2 | 0.66 | 10% | 0.72 | 0.67 | 32 L/s | IU-SF-03 WS-09 | 2.29 | 1.74 | 140 L/s | 6% | 0.76 | 2.9 / 0.3 |
| Z-SF-04 | SF-16 | wall_split | 17 | 0.67 | 0.23 | 0.9 | 10% | 0.99 | 0.94 | 51 L/s | IU-SF-04 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.35 |
| Z-SF-05 | SF-17 | wall_split | 15 | 0.57 | 0.25 | 0.82 | 10% | 0.9 | 0.85 | 45 L/s | IU-SF-05 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.35 |
| Z-SF-06 | SF-19 | wall_split | 17 | 0.67 | 0.23 | 0.91 | 10% | 1.0 | 0.94 | 51 L/s | IU-SF-06 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.35 |
| Z-SF-07 | SF-22 | wall_split | 15 | 0.57 | 0.25 | 0.82 | 10% | 0.91 | 0.85 | 45 L/s | IU-SF-07 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.35 |
| Z-SF-08 | SF-30 | wall_split | 17 | 0.67 | 0.23 | 0.9 | 10% | 0.99 | 0.93 | 49 L/s | IU-SF-08 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.42 |
| Z-SF-09 | SF-31 | wall_split | 15 | 0.63 | 0.25 | 0.88 | 10% | 0.96 | 0.91 | 46 L/s | IU-SF-09 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.42 |
| Z-SF-10 | SF-06 | ducted_split | 15 | 1.97 | 0.99 | 2.95 | 10% | 3.25 | 2.75 | 121 L/s | IU-SF-10 DS-18 | 4.66 | 3.5 | 300 L/s | 13% | 1.66 | 5.8 / 1.11 |
| Z-SF-11 | SF-10 | ducted_split | 15 | 2.06 | 0.99 | 3.05 | 10% | 3.35 | 2.86 | 128 L/s | IU-SF-11 DS-18 | 4.66 | 3.5 | 300 L/s | 13% | 1.66 | 5.8 / 1.16 |
| Z-SF-12 | SF-24 | ducted_split | 15 | 1.96 | 0.99 | 2.95 | 10% | 3.24 | 2.75 | 120 L/s | IU-SF-12 DS-18 | 4.66 | 3.5 | 300 L/s | 13% | 1.66 | 5.8 / 1.11 |
| Z-SF-13 | SF-28 | ducted_split | 15 | 1.98 | 0.99 | 2.96 | 10% | 3.26 | 2.76 | 122 L/s | IU-SF-13 DS-18 | 4.66 | 3.5 | 300 L/s | 13% | 1.66 | 5.8 / 1.12 |
| Z-TF-01 | TF-05 | wall_split | 17 | 0.82 | 0.23 | 1.05 | 10% | 1.16 | 1.1 | 62 L/s | IU-TF-01 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.5 |
| Z-TF-02 | TF-06 | wall_split | 15 | 0.7 | 0.25 | 0.95 | 10% | 1.05 | 0.99 | 52 L/s | IU-TF-02 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.46 |
| Z-TF-03 | TF-16 | wall_split | 17 | 0.73 | 0.23 | 0.96 | 10% | 1.06 | 1.0 | 56 L/s | IU-TF-03 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.38 |
| Z-TF-04 | TF-17 | wall_split | 15 | 0.63 | 0.25 | 0.88 | 10% | 0.97 | 0.91 | 48 L/s | IU-TF-04 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.38 |
| Z-TF-05 | TF-18 | wall_split | 17 | 0.73 | 0.23 | 0.97 | 10% | 1.06 | 1.01 | 56 L/s | IU-TF-05 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.38 |
| Z-TF-06 | TF-21 | wall_split | 15 | 0.63 | 0.25 | 0.88 | 10% | 0.97 | 0.92 | 48 L/s | IU-TF-06 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.38 |
| Z-TF-07 | TF-29 | wall_split | 17 | 0.81 | 0.23 | 1.05 | 10% | 1.15 | 1.1 | 61 L/s | IU-TF-07 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.5 |
| Z-TF-08 | TF-30 | wall_split | 15 | 0.78 | 0.25 | 1.03 | 10% | 1.13 | 1.07 | 58 L/s | IU-TF-08 WS-09 | 2.29 | 1.74 | 140 L/s | 7% | 0.76 | 2.9 / 0.5 |
| Z-TF-09 | TF-08 | ducted_split | 15 | 2.15 | 0.99 | 3.14 | 10% | 3.45 | 2.95 | 136 L/s | IU-TF-09 DS-18 | 4.66 | 3.5 | 300 L/s | 13% | 1.66 | 5.8 / 1.2 |
| Z-TF-10 | TF-12 | ducted_split | 15 | 2.1 | 0.98 | 3.08 | 10% | 3.39 | 2.9 | 132 L/s | IU-TF-10 DS-18 | 4.66 | 3.5 | 300 L/s | 13% | 1.66 | 5.8 / 1.18 |
| Z-TF-11 | TF-23 | ducted_split | 15 | 2.08 | 0.99 | 3.07 | 10% | 3.37 | 2.88 | 130 L/s | IU-TF-11 DS-18 | 4.66 | 3.5 | 300 L/s | 13% | 1.66 | 5.8 / 1.17 |
| Z-TF-12 | TF-27 | ducted_split | 15 | 2.02 | 0.98 | 3.0 | 10% | 3.3 | 2.8 | 125 L/s | IU-TF-12 DS-18 | 4.66 | 3.5 | 300 L/s | 13% | 1.66 | 5.8 / 1.13 |

| Tag | Model | System | Serves | Nominal | Input kW | Location |
| --- | --- | --- | --- | --- | --- | --- |
| ODU-01 | WS-O-09 | wall_split | IU-GF-01 | 2.6 kW | 0.76 | GF |
| ODU-02 | WS-O-09 | wall_split | IU-GF-02 | 2.6 kW | 0.76 | GF |
| ODU-03 | WS-O-09 | wall_split | IU-GF-03 | 2.6 kW | 0.76 | GF |
| ODU-04 | WS-O-09 | wall_split | IU-GF-04 | 2.6 kW | 0.76 | GF |
| ODU-05 | WS-O-09 | wall_split | IU-GF-05 | 2.6 kW | 0.76 | GF |
| ODU-06 | WS-O-09 | wall_split | IU-GF-06 | 2.6 kW | 0.76 | GF |
| ODU-07 | WS-O-09 | wall_split | IU-GF-07 | 2.6 kW | 0.76 | GF |
| ODU-08 | WS-O-09 | wall_split | IU-GF-08 | 2.6 kW | 0.76 | GF |
| ODU-09 | DS-O-18 | ducted_split | IU-GF-09 | 5.3 kW | 1.66 | RF |
| ODU-10 | DS-O-18 | ducted_split | IU-GF-10 | 5.3 kW | 1.66 | RF |
| ODU-11 | DS-O-18 | ducted_split | IU-GF-11 | 5.3 kW | 1.66 | RF |
| ODU-12 | DS-O-18 | ducted_split | IU-GF-12 | 5.3 kW | 1.66 | RF |
| ODU-13 | WS-O-09 | wall_split | IU-FF-01 | 2.6 kW | 0.76 | FF |
| ODU-14 | WS-O-09 | wall_split | IU-FF-02 | 2.6 kW | 0.76 | FF |
| ODU-15 | WS-O-09 | wall_split | IU-FF-03 | 2.6 kW | 0.76 | FF |
| ODU-16 | WS-O-09 | wall_split | IU-FF-04 | 2.6 kW | 0.76 | FF |
| ODU-17 | WS-O-09 | wall_split | IU-FF-05 | 2.6 kW | 0.76 | FF |
| ODU-18 | WS-O-09 | wall_split | IU-FF-06 | 2.6 kW | 0.76 | FF |
| ODU-19 | WS-O-09 | wall_split | IU-FF-07 | 2.6 kW | 0.76 | FF |
| ODU-20 | WS-O-09 | wall_split | IU-FF-08 | 2.6 kW | 0.76 | FF |
| ODU-21 | DS-O-18 | ducted_split | IU-FF-09 | 5.3 kW | 1.66 | RF |
| ODU-22 | DS-O-18 | ducted_split | IU-FF-10 | 5.3 kW | 1.66 | RF |
| ODU-23 | DS-O-18 | ducted_split | IU-FF-11 | 5.3 kW | 1.66 | RF |
| ODU-24 | DS-O-18 | ducted_split | IU-FF-12 | 5.3 kW | 1.66 | RF |
| ODU-25 | WS-O-09 | wall_split | IU-SF-01 | 2.6 kW | 0.76 | SF |
| ODU-26 | WS-O-09 | wall_split | IU-SF-02 | 2.6 kW | 0.76 | SF |
| ODU-27 | WS-O-09 | wall_split | IU-SF-03 | 2.6 kW | 0.76 | SF |
| ODU-28 | WS-O-09 | wall_split | IU-SF-04 | 2.6 kW | 0.76 | SF |
| ODU-29 | WS-O-09 | wall_split | IU-SF-05 | 2.6 kW | 0.76 | SF |
| ODU-30 | WS-O-09 | wall_split | IU-SF-06 | 2.6 kW | 0.76 | SF |
| ODU-31 | WS-O-09 | wall_split | IU-SF-07 | 2.6 kW | 0.76 | SF |
| ODU-32 | WS-O-09 | wall_split | IU-SF-08 | 2.6 kW | 0.76 | SF |
| ODU-33 | WS-O-09 | wall_split | IU-SF-09 | 2.6 kW | 0.76 | SF |
| ODU-34 | DS-O-18 | ducted_split | IU-SF-10 | 5.3 kW | 1.66 | RF |
| ODU-35 | DS-O-18 | ducted_split | IU-SF-11 | 5.3 kW | 1.66 | RF |
| ODU-36 | DS-O-18 | ducted_split | IU-SF-12 | 5.3 kW | 1.66 | RF |
| ODU-37 | DS-O-18 | ducted_split | IU-SF-13 | 5.3 kW | 1.66 | RF |
| ODU-38 | WS-O-09 | wall_split | IU-TF-01 | 2.6 kW | 0.76 | TF |
| ODU-39 | WS-O-09 | wall_split | IU-TF-02 | 2.6 kW | 0.76 | TF |
| ODU-40 | WS-O-09 | wall_split | IU-TF-03 | 2.6 kW | 0.76 | TF |
| ODU-41 | WS-O-09 | wall_split | IU-TF-04 | 2.6 kW | 0.76 | TF |
| ODU-42 | WS-O-09 | wall_split | IU-TF-05 | 2.6 kW | 0.76 | TF |
| ODU-43 | WS-O-09 | wall_split | IU-TF-06 | 2.6 kW | 0.76 | TF |
| ODU-44 | WS-O-09 | wall_split | IU-TF-07 | 2.6 kW | 0.76 | TF |
| ODU-45 | WS-O-09 | wall_split | IU-TF-08 | 2.6 kW | 0.76 | TF |
| ODU-46 | DS-O-18 | ducted_split | IU-TF-09 | 5.3 kW | 1.66 | RF |
| ODU-47 | DS-O-18 | ducted_split | IU-TF-10 | 5.3 kW | 1.66 | RF |
| ODU-48 | DS-O-18 | ducted_split | IU-TF-11 | 5.3 kW | 1.66 | RF |
| ODU-49 | DS-O-18 | ducted_split | IU-TF-12 | 5.3 kW | 1.66 | RF |

# 6. Duct sizing and air terminals

Equal friction method, target 0.80 Pa/m, velocity limits (m/s) {'main': 5.0, 'branch': 3.5, 'runout': 2.5, 'return': 3.5, 'fresh_air': 4.0, 'exhaust': 4.0}. Darcy-Weisbach with Altshul-Tsal friction factor, roughness 0.09 mm; rectangular sizes from De = 1.30(ab)^0.625/(a+b)^0.25; fittings +50% equivalent length.

Code reference: ASHRAE Fundamentals 2021 Ch.21 (equal friction method, Eq.18-19 Altshul-Tsal); SBC 501 §603.4 metallic ducts; SMACNA 2005 Tables 2-1/2-2 (gauge)

### Z-GF-09 - IU-GF-09 (GF)

| Segment | Type | Serves | Flow | Size | De mm | Velocity | Friction | Length m | Δp | Gauge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D-GF-001 | main | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 0.83 | 0.9 Pa | 26 ga (0.55 mm) |
| D-GF-002 | branch | GF-25 | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 0.22 | 0.1 Pa | 24 ga (0.70 mm) |
| D-GF-003 | runout | GF-25 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.67 | 0.5 Pa | 26 ga (0.55 mm) |
| D-GF-004 | runout | GF-25 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.67 | 0.5 Pa | 26 ga (0.55 mm) |
| D-GF-005 | main | - | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 1.2 | 0.7 Pa | 24 ga (0.70 mm) |
| D-GF-006 | main | - | 32 L/s | Ø125 round | 125 | 2.60 m/s | 0.89 Pa/m | 2.46 | 3.3 Pa | 26 ga (0.55 mm) |

Critical path: required ESP 67 Pa vs available 75 Pa - OK.

### Z-GF-10 - IU-GF-10 (GF)

| Segment | Type | Serves | Flow | Size | De mm | Velocity | Friction | Length m | Δp | Gauge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D-GF-007 | main | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 0.83 | 0.9 Pa | 26 ga (0.55 mm) |
| D-GF-008 | branch | GF-26 | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 0.25 | 0.1 Pa | 24 ga (0.70 mm) |
| D-GF-009 | runout | GF-26 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.67 | 0.5 Pa | 26 ga (0.55 mm) |
| D-GF-010 | runout | GF-26 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.67 | 0.5 Pa | 26 ga (0.55 mm) |
| D-GF-011 | main | - | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 1.2 | 0.7 Pa | 24 ga (0.70 mm) |
| D-GF-012 | main | - | 32 L/s | Ø125 round | 125 | 2.60 m/s | 0.89 Pa/m | 1.8 | 2.4 Pa | 26 ga (0.55 mm) |

Critical path: required ESP 67 Pa vs available 75 Pa - OK.

### Z-GF-11 - IU-GF-11 (GF)

| Segment | Type | Serves | Flow | Size | De mm | Velocity | Friction | Length m | Δp | Gauge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D-GF-013 | main | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 0.82 | 0.9 Pa | 26 ga (0.55 mm) |
| D-GF-014 | branch | GF-31 | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 0.14 | 0.1 Pa | 24 ga (0.70 mm) |
| D-GF-015 | runout | GF-31 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.67 | 0.5 Pa | 26 ga (0.55 mm) |
| D-GF-016 | runout | GF-31 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.67 | 0.5 Pa | 26 ga (0.55 mm) |
| D-GF-017 | main | - | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 1.2 | 0.7 Pa | 24 ga (0.70 mm) |
| D-GF-018 | main | - | 32 L/s | Ø125 round | 125 | 2.59 m/s | 0.89 Pa/m | 2.19 | 2.9 Pa | 26 ga (0.55 mm) |

Critical path: required ESP 67 Pa vs available 75 Pa - OK.

### Z-GF-12 - IU-GF-12 (GF)

| Segment | Type | Serves | Flow | Size | De mm | Velocity | Friction | Length m | Δp | Gauge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D-GF-019 | main | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 0.83 | 0.9 Pa | 26 ga (0.55 mm) |
| D-GF-020 | branch | GF-32 | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 0.16 | 0.1 Pa | 24 ga (0.70 mm) |
| D-GF-021 | runout | GF-32 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.67 | 0.5 Pa | 26 ga (0.55 mm) |
| D-GF-022 | runout | GF-32 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.67 | 0.5 Pa | 26 ga (0.55 mm) |
| D-GF-023 | main | - | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 1.2 | 0.7 Pa | 24 ga (0.70 mm) |
| D-GF-024 | main | - | 32 L/s | Ø125 round | 125 | 2.59 m/s | 0.89 Pa/m | 2.15 | 2.9 Pa | 26 ga (0.55 mm) |

Critical path: required ESP 67 Pa vs available 75 Pa - OK.

### Z-FF-09 - IU-FF-09 (FF)

| Segment | Type | Serves | Flow | Size | De mm | Velocity | Friction | Length m | Δp | Gauge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D-FF-001 | main | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 0.82 | 0.9 Pa | 26 ga (0.55 mm) |
| D-FF-002 | branch | FF-04 | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 0.14 | 0.1 Pa | 24 ga (0.70 mm) |
| D-FF-003 | runout | FF-04 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.67 | 0.5 Pa | 26 ga (0.55 mm) |
| D-FF-004 | runout | FF-04 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.67 | 0.5 Pa | 26 ga (0.55 mm) |
| D-FF-005 | main | - | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 1.2 | 0.7 Pa | 24 ga (0.70 mm) |
| D-FF-006 | main | - | 32 L/s | Ø125 round | 125 | 2.59 m/s | 0.89 Pa/m | 2.48 | 3.3 Pa | 26 ga (0.55 mm) |

Critical path: required ESP 67 Pa vs available 75 Pa - OK.

### Z-FF-10 - IU-FF-10 (FF)

| Segment | Type | Serves | Flow | Size | De mm | Velocity | Friction | Length m | Δp | Gauge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D-FF-007 | main | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 0.83 | 0.9 Pa | 26 ga (0.55 mm) |
| D-FF-008 | branch | FF-05 | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 0.16 | 0.1 Pa | 24 ga (0.70 mm) |
| D-FF-009 | runout | FF-05 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.67 | 0.5 Pa | 26 ga (0.55 mm) |
| D-FF-010 | runout | FF-05 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.67 | 0.5 Pa | 26 ga (0.55 mm) |
| D-FF-011 | main | - | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 1.2 | 0.7 Pa | 24 ga (0.70 mm) |
| D-FF-012 | main | - | 32 L/s | Ø125 round | 125 | 2.59 m/s | 0.89 Pa/m | 2.48 | 3.3 Pa | 26 ga (0.55 mm) |

Critical path: required ESP 67 Pa vs available 75 Pa - OK.

### Z-FF-11 - IU-FF-11 (FF)

| Segment | Type | Serves | Flow | Size | De mm | Velocity | Friction | Length m | Δp | Gauge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D-FF-013 | main | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 0.84 | 0.9 Pa | 26 ga (0.55 mm) |
| D-FF-014 | branch | FF-26 | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 0.15 | 0.1 Pa | 24 ga (0.70 mm) |
| D-FF-015 | runout | FF-26 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.67 | 0.5 Pa | 26 ga (0.55 mm) |
| D-FF-016 | runout | FF-26 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.67 | 0.5 Pa | 26 ga (0.55 mm) |
| D-FF-017 | main | - | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 1.2 | 0.7 Pa | 24 ga (0.70 mm) |
| D-FF-018 | main | - | 32 L/s | Ø125 round | 125 | 2.59 m/s | 0.89 Pa/m | 2.48 | 3.3 Pa | 26 ga (0.55 mm) |

Critical path: required ESP 67 Pa vs available 75 Pa - OK.

### Z-FF-12 - IU-FF-12 (FF)

| Segment | Type | Serves | Flow | Size | De mm | Velocity | Friction | Length m | Δp | Gauge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D-FF-019 | main | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 0.83 | 0.9 Pa | 26 ga (0.55 mm) |
| D-FF-020 | branch | FF-27 | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 0.16 | 0.1 Pa | 24 ga (0.70 mm) |
| D-FF-021 | runout | FF-27 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.67 | 0.5 Pa | 26 ga (0.55 mm) |
| D-FF-022 | runout | FF-27 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.67 | 0.5 Pa | 26 ga (0.55 mm) |
| D-FF-023 | main | - | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 1.2 | 0.7 Pa | 24 ga (0.70 mm) |
| D-FF-024 | main | - | 32 L/s | Ø125 round | 125 | 2.59 m/s | 0.89 Pa/m | 2.5 | 3.3 Pa | 26 ga (0.55 mm) |

Critical path: required ESP 67 Pa vs available 75 Pa - OK.

### Z-SF-10 - IU-SF-10 (SF)

| Segment | Type | Serves | Flow | Size | De mm | Velocity | Friction | Length m | Δp | Gauge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D-SF-001 | riser | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 1.07 | 1.2 Pa | 26 ga (0.55 mm) |
| D-SF-002 | main | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 0.11 | 0.1 Pa | 26 ga (0.55 mm) |
| D-SF-003 | runout | SF-06 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.89 | 0.6 Pa | 26 ga (0.55 mm) |
| D-SF-004 | runout | SF-06 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.89 | 0.6 Pa | 26 ga (0.55 mm) |
| D-SF-005 | main | - | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 1.2 | 0.7 Pa | 24 ga (0.70 mm) |
| D-SF-006 | main | - | 40 L/s | Ø150 round | 150 | 2.26 m/s | 0.55 Pa/m | 2.57 | 2.1 Pa | 26 ga (0.55 mm) |

Critical path: required ESP 68 Pa vs available 75 Pa - OK.

### Z-SF-11 - IU-SF-11 (SF)

| Segment | Type | Serves | Flow | Size | De mm | Velocity | Friction | Length m | Δp | Gauge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D-SF-007 | riser | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 0.93 | 1.0 Pa | 26 ga (0.55 mm) |
| D-SF-008 | main | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 0.11 | 0.1 Pa | 26 ga (0.55 mm) |
| D-SF-009 | runout | SF-10 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.89 | 0.6 Pa | 26 ga (0.55 mm) |
| D-SF-010 | runout | SF-10 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.89 | 0.6 Pa | 26 ga (0.55 mm) |
| D-SF-011 | main | - | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 1.2 | 0.7 Pa | 24 ga (0.70 mm) |
| D-SF-012 | main | - | 40 L/s | Ø150 round | 150 | 2.26 m/s | 0.55 Pa/m | 2.44 | 2.0 Pa | 26 ga (0.55 mm) |

Critical path: required ESP 67 Pa vs available 75 Pa - OK.

### Z-SF-12 - IU-SF-12 (SF)

| Segment | Type | Serves | Flow | Size | De mm | Velocity | Friction | Length m | Δp | Gauge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D-SF-013 | main | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 0.11 | 0.1 Pa | 26 ga (0.55 mm) |
| D-SF-014 | branch | SF-24 | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 1.07 | 0.6 Pa | 24 ga (0.70 mm) |
| D-SF-015 | runout | SF-24 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.89 | 0.6 Pa | 26 ga (0.55 mm) |
| D-SF-016 | runout | SF-24 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.89 | 0.6 Pa | 26 ga (0.55 mm) |
| D-SF-017 | main | - | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 1.2 | 0.7 Pa | 24 ga (0.70 mm) |
| D-SF-018 | main | - | 40 L/s | Ø150 round | 150 | 2.26 m/s | 0.55 Pa/m | 2.56 | 2.1 Pa | 26 ga (0.55 mm) |

Critical path: required ESP 67 Pa vs available 75 Pa - OK.

### Z-SF-13 - IU-SF-13 (SF)

| Segment | Type | Serves | Flow | Size | De mm | Velocity | Friction | Length m | Δp | Gauge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D-SF-019 | riser | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 0.11 | 0.1 Pa | 26 ga (0.55 mm) |
| D-SF-020 | main | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 0.94 | 1.0 Pa | 26 ga (0.55 mm) |
| D-SF-021 | runout | SF-28 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.89 | 0.6 Pa | 26 ga (0.55 mm) |
| D-SF-022 | runout | SF-28 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.89 | 0.6 Pa | 26 ga (0.55 mm) |
| D-SF-023 | main | - | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 1.2 | 0.7 Pa | 24 ga (0.70 mm) |
| D-SF-024 | main | - | 40 L/s | Ø150 round | 150 | 2.26 m/s | 0.55 Pa/m | 2.43 | 2.0 Pa | 26 ga (0.55 mm) |

Critical path: required ESP 67 Pa vs available 75 Pa - OK.

### Z-TF-09 - IU-TF-09 (TF)

| Segment | Type | Serves | Flow | Size | De mm | Velocity | Friction | Length m | Δp | Gauge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D-TF-001 | riser | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 1.05 | 1.2 Pa | 26 ga (0.55 mm) |
| D-TF-002 | main | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 0.1 | 0.1 Pa | 26 ga (0.55 mm) |
| D-TF-003 | runout | TF-08 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.91 | 0.6 Pa | 26 ga (0.55 mm) |
| D-TF-004 | runout | TF-08 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.91 | 0.6 Pa | 26 ga (0.55 mm) |
| D-TF-005 | main | - | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 1.2 | 0.7 Pa | 24 ga (0.70 mm) |
| D-TF-006 | main | - | 40 L/s | Ø150 round | 150 | 2.26 m/s | 0.55 Pa/m | 2.4 | 2.0 Pa | 26 ga (0.55 mm) |

Critical path: required ESP 68 Pa vs available 75 Pa - OK.

### Z-TF-10 - IU-TF-10 (TF)

| Segment | Type | Serves | Flow | Size | De mm | Velocity | Friction | Length m | Δp | Gauge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D-TF-007 | riser | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 1.06 | 1.2 Pa | 26 ga (0.55 mm) |
| D-TF-008 | main | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 0.09 | 0.1 Pa | 26 ga (0.55 mm) |
| D-TF-009 | runout | TF-12 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.91 | 0.6 Pa | 26 ga (0.55 mm) |
| D-TF-010 | runout | TF-12 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.91 | 0.6 Pa | 26 ga (0.55 mm) |
| D-TF-011 | main | - | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 1.2 | 0.7 Pa | 24 ga (0.70 mm) |
| D-TF-012 | main | - | 40 L/s | Ø150 round | 150 | 2.25 m/s | 0.55 Pa/m | 2.4 | 2.0 Pa | 26 ga (0.55 mm) |

Critical path: required ESP 68 Pa vs available 75 Pa - OK.

### Z-TF-11 - IU-TF-11 (TF)

| Segment | Type | Serves | Flow | Size | De mm | Velocity | Friction | Length m | Δp | Gauge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D-TF-013 | riser | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 1.07 | 1.2 Pa | 26 ga (0.55 mm) |
| D-TF-014 | main | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 0.1 | 0.1 Pa | 26 ga (0.55 mm) |
| D-TF-015 | runout | TF-23 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.92 | 0.6 Pa | 26 ga (0.55 mm) |
| D-TF-016 | runout | TF-23 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.92 | 0.6 Pa | 26 ga (0.55 mm) |
| D-TF-017 | main | - | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 1.2 | 0.7 Pa | 24 ga (0.70 mm) |
| D-TF-018 | main | - | 40 L/s | Ø150 round | 150 | 2.26 m/s | 0.55 Pa/m | 2.35 | 1.9 Pa | 26 ga (0.55 mm) |

Critical path: required ESP 68 Pa vs available 75 Pa - OK.

### Z-TF-12 - IU-TF-12 (TF)

| Segment | Type | Serves | Flow | Size | De mm | Velocity | Friction | Length m | Δp | Gauge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| D-TF-019 | riser | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 1.05 | 1.2 Pa | 26 ga (0.55 mm) |
| D-TF-020 | main | - | 300 L/s | 300x250 | 299 | 4.00 m/s | 0.73 Pa/m | 0.09 | 0.1 Pa | 26 ga (0.55 mm) |
| D-TF-021 | runout | TF-27 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.92 | 0.6 Pa | 26 ga (0.55 mm) |
| D-TF-022 | runout | TF-27 | 150 L/s | Ø300 round | 300 | 2.12 m/s | 0.21 Pa/m | 1.92 | 0.6 Pa | 26 ga (0.55 mm) |
| D-TF-023 | main | - | 300 L/s | 400x250 | 343 | 3.00 m/s | 0.38 Pa/m | 1.2 | 0.7 Pa | 24 ga (0.70 mm) |
| D-TF-024 | main | - | 40 L/s | Ø150 round | 150 | 2.25 m/s | 0.55 Pa/m | 2.4 | 2.0 Pa | 26 ga (0.55 mm) |

Critical path: required ESP 68 Pa vs available 75 Pa - OK.

## 6.1 Supply diffuser schedule

| Tag | Room | Model | Flow | NC | Throw m |
| --- | --- | --- | --- | --- | --- |
| SD-GF-01 | GF-25 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-GF-02 | GF-25 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-GF-03 | GF-26 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-GF-04 | GF-26 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-GF-05 | GF-31 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-GF-06 | GF-31 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-GF-07 | GF-32 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-GF-08 | GF-32 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-FF-01 | FF-04 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-FF-02 | FF-04 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-FF-03 | FF-05 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-FF-04 | FF-05 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-FF-05 | FF-26 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-FF-06 | FF-26 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-FF-07 | FF-27 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-FF-08 | FF-27 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-SF-01 | SF-06 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-SF-02 | SF-06 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-SF-03 | SF-10 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-SF-04 | SF-10 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-SF-05 | SF-24 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-SF-06 | SF-24 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-SF-07 | SF-28 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-SF-08 | SF-28 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-TF-01 | TF-08 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-TF-02 | TF-08 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-TF-03 | TF-12 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-TF-04 | TF-12 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-TF-05 | TF-23 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-TF-06 | TF-23 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-TF-07 | TF-27 | SD-250 | 150 L/s | 22 | 2.2 |
| SD-TF-08 | TF-27 | SD-250 | 150 L/s | 22 | 2.2 |

Code reference: ASHRAE Applications 2019 Ch.49 Table 1 (design NC)

## 6.2 Exhaust systems

| Fan | Room | Flow | Model | Duct | Length m | Velocity | ESP req. | Discharge | Clause |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| EF-GF-01 | GF-04 | 50 L/s | EF-50 | Ø150 | 1.32 | 2.83 m/s | 42 Pa | wall_louver | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| EF-GF-02 | GF-05 | 25 L/s | EF-25 | Ø125 | 1.37 | 2.04 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-GF-03 | GF-06 | 25 L/s | EF-25 | Ø125 | 1.32 | 2.04 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-GF-04 | GF-08 | 25 L/s | EF-25 | Ø125 | 0.52 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-GF-05 | GF-09 | 25 L/s | EF-25 | Ø125 | 2.14 | 2.04 m/s | 42 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-GF-06 | GF-17 | 50 L/s | EF-50 | Ø150 | 1.28 | 2.83 m/s | 42 Pa | wall_louver | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| EF-GF-07 | GF-18 | 25 L/s | EF-25 | Ø125 | 0.57 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-GF-08 | GF-19 | 25 L/s | EF-25 | Ø125 | 0.52 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-GF-09 | GF-21 | 25 L/s | EF-25 | Ø125 | 0.53 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-GF-10 | GF-22 | 25 L/s | EF-25 | Ø125 | 0.56 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-GF-11 | GF-23 | 50 L/s | EF-50 | Ø150 | 1.27 | 2.83 m/s | 42 Pa | wall_louver | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| EF-GF-12 | GF-33 | 25 L/s | EF-25 | Ø125 | 1.36 | 2.04 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-GF-13 | GF-34 | 25 L/s | EF-25 | Ø125 | 1.33 | 2.04 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-GF-14 | GF-36 | 25 L/s | EF-25 | Ø125 | 1.35 | 2.04 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-GF-15 | GF-37 | 50 L/s | EF-50 | Ø150 | 0.87 | 2.83 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| EF-FF-01 | FF-07 | 50 L/s | EF-50 | Ø150 | 0.81 | 2.83 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| EF-FF-02 | FF-08 | 25 L/s | EF-25 | Ø125 | 0.56 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-FF-03 | FF-09 | 25 L/s | EF-25 | Ø125 | 0.54 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-FF-04 | FF-11 | 25 L/s | EF-25 | Ø125 | 0.53 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-FF-05 | FF-12 | 25 L/s | EF-25 | Ø125 | 0.55 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-FF-06 | FF-13 | 50 L/s | EF-50 | Ø150 | 0.87 | 2.83 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| EF-FF-07 | FF-18 | 50 L/s | EF-50 | Ø150 | 0.81 | 2.83 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| EF-FF-08 | FF-19 | 25 L/s | EF-25 | Ø125 | 0.57 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-FF-09 | FF-20 | 25 L/s | EF-25 | Ø125 | 0.52 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-FF-10 | FF-22 | 25 L/s | EF-25 | Ø125 | 0.53 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-FF-11 | FF-23 | 25 L/s | EF-25 | Ø125 | 0.56 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-FF-12 | FF-24 | 50 L/s | EF-50 | Ø150 | 0.82 | 2.83 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| EF-SF-01 | SF-05 | 50 L/s | EF-50 | Ø150 | 0.92 | 2.83 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| EF-SF-02 | SF-07 | 25 L/s | EF-25 | Ø125 | 0.64 | 2.04 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-SF-03 | SF-09 | 25 L/s | EF-25 | Ø125 | 0.63 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-SF-04 | SF-11 | 50 L/s | EF-50 | Ø150 | 1.52 | 2.83 m/s | 42 Pa | wall_louver | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| EF-SF-05 | SF-12 | 50 L/s | EF-50 | Ø150 | 1.14 | 2.83 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| EF-SF-06 | SF-13 | 25 L/s | EF-25 | Ø125 | 0.61 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-SF-07 | SF-14 | 25 L/s | EF-25 | Ø125 | 0.59 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-SF-08 | SF-20 | 25 L/s | EF-25 | Ø125 | 0.59 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-SF-09 | SF-21 | 25 L/s | EF-25 | Ø125 | 0.6 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-SF-10 | SF-23 | 50 L/s | EF-50 | Ø150 | 0.92 | 2.83 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| EF-SF-11 | SF-25 | 25 L/s | EF-25 | Ø125 | 0.64 | 2.04 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-SF-12 | SF-27 | 25 L/s | EF-25 | Ø125 | 0.63 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-SF-13 | SF-29 | 50 L/s | EF-50 | Ø150 | 0.98 | 2.83 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| EF-TF-01 | TF-07 | 50 L/s | EF-50 | Ø150 | 0.92 | 2.83 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| EF-TF-02 | TF-09 | 25 L/s | EF-25 | Ø125 | 0.63 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-TF-03 | TF-11 | 25 L/s | EF-25 | Ø125 | 0.63 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-TF-04 | TF-13 | 50 L/s | EF-50 | Ø150 | 0.98 | 2.83 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| EF-TF-05 | TF-14 | 25 L/s | EF-25 | Ø125 | 0.61 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-TF-06 | TF-15 | 25 L/s | EF-25 | Ø125 | 0.59 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-TF-07 | TF-19 | 25 L/s | EF-25 | Ø125 | 0.59 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-TF-08 | TF-20 | 25 L/s | EF-25 | Ø125 | 0.6 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-TF-09 | TF-22 | 50 L/s | EF-50 | Ø150 | 0.92 | 2.83 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| EF-TF-10 | TF-24 | 25 L/s | EF-25 | Ø125 | 0.64 | 2.04 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-TF-11 | TF-26 | 25 L/s | EF-25 | Ø125 | 0.63 | 2.04 m/s | 40 Pa | wall_louver | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| EF-TF-12 | TF-28 | 50 L/s | EF-50 | Ø150 | 0.98 | 2.83 m/s | 41 Pa | wall_louver | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |

# 7. Piping

## 7.1 Refrigerant piping

| Run | Unit → ODU | Capacity | Liquid / gas OD mm | Horiz. floor m | Vertical m | Roof m | Total m | Limit m | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| RP-IU-GF-01 | IU-GF-01 → ODU-01 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 1.47 | 0.5 | 0.0 | 2.2 | 25 | OK |
| RP-IU-GF-02 | IU-GF-02 → ODU-02 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 0.61 | 0.5 | 0.0 | 1.2 | 25 | OK |
| RP-IU-GF-03 | IU-GF-03 → ODU-03 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 1.15 | 0.5 | 0.0 | 1.8 | 25 | OK |
| RP-IU-GF-04 | IU-GF-04 → ODU-04 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 0.62 | 0.5 | 0.0 | 1.2 | 25 | OK |
| RP-IU-GF-05 | IU-GF-05 → ODU-05 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 1.08 | 0.5 | 0.0 | 1.7 | 25 | OK |
| RP-IU-GF-06 | IU-GF-06 → ODU-06 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 0.91 | 0.5 | 0.0 | 1.6 | 25 | OK |
| RP-IU-GF-07 | IU-GF-07 → ODU-07 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 1.49 | 0.5 | 0.0 | 2.2 | 25 | OK |
| RP-IU-GF-08 | IU-GF-08 → ODU-08 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 1.33 | 0.5 | 0.0 | 2.0 | 25 | OK |
| RP-IU-GF-09 | IU-GF-09 → ODU-09 | 5.3 kW | 6.35 / 12.7 (1/4" / 1/2") | 4.07 | 13.5 | 25.78 | 47.7 | 50 | OK |
| RP-IU-GF-10 | IU-GF-10 → ODU-10 | 5.3 kW | 6.35 / 12.7 (1/4" / 1/2") | 4.08 | 13.5 | 27.3 | 49.4 | 50 | OK |
| RP-IU-GF-11 | IU-GF-11 → ODU-11 | 5.3 kW | 6.35 / 12.7 (1/4" / 1/2") | 4.06 | 13.5 | 17.85 | 39.0 | 50 | OK |
| RP-IU-GF-12 | IU-GF-12 → ODU-12 | 5.3 kW | 6.35 / 12.7 (1/4" / 1/2") | 4.07 | 13.5 | 17.92 | 39.0 | 50 | OK |
| RP-IU-FF-01 | IU-FF-01 → ODU-13 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 3.64 | 0.5 | 0.0 | 4.6 | 25 | OK |
| RP-IU-FF-02 | IU-FF-02 → ODU-14 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 2.63 | 0.5 | 0.0 | 3.4 | 25 | OK |
| RP-IU-FF-03 | IU-FF-03 → ODU-15 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 1.33 | 0.5 | 0.0 | 2.0 | 25 | OK |
| RP-IU-FF-04 | IU-FF-04 → ODU-16 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 0.61 | 0.5 | 0.0 | 1.2 | 25 | OK |
| RP-IU-FF-05 | IU-FF-05 → ODU-17 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 1.14 | 0.5 | 0.0 | 1.8 | 25 | OK |
| RP-IU-FF-06 | IU-FF-06 → ODU-18 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 1.12 | 0.5 | 0.0 | 1.8 | 25 | OK |
| RP-IU-FF-07 | IU-FF-07 → ODU-19 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 2.61 | 0.5 | 0.0 | 3.4 | 25 | OK |
| RP-IU-FF-08 | IU-FF-08 → ODU-20 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 3.66 | 0.5 | 0.0 | 4.6 | 25 | OK |
| RP-IU-FF-09 | IU-FF-09 → ODU-21 | 5.3 kW | 6.35 / 12.7 (1/4" / 1/2") | 5.13 | 10.5 | 5.02 | 22.7 | 50 | OK |
| RP-IU-FF-10 | IU-FF-10 → ODU-22 | 5.3 kW | 6.35 / 12.7 (1/4" / 1/2") | 5.16 | 10.5 | 10.88 | 29.2 | 50 | OK |
| RP-IU-FF-11 | IU-FF-11 → ODU-23 | 5.3 kW | 6.35 / 12.7 (1/4" / 1/2") | 5.15 | 10.5 | 17.73 | 36.7 | 50 | OK |
| RP-IU-FF-12 | IU-FF-12 → ODU-24 | 5.3 kW | 6.35 / 12.7 (1/4" / 1/2") | 5.16 | 10.5 | 11.79 | 30.2 | 50 | OK |
| RP-IU-SF-01 | IU-SF-01 → ODU-25 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 4.09 | 0.5 | 0.0 | 5.0 | 25 | OK |
| RP-IU-SF-02 | IU-SF-02 → ODU-26 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 0.61 | 0.5 | 0.0 | 1.2 | 25 | OK |
| RP-IU-SF-03 | IU-SF-03 → ODU-27 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 2.57 | 0.5 | 0.0 | 3.4 | 25 | OK |
| RP-IU-SF-04 | IU-SF-04 → ODU-28 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 1.19 | 0.5 | 0.0 | 1.9 | 25 | OK |
| RP-IU-SF-05 | IU-SF-05 → ODU-29 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 1.18 | 0.5 | 0.0 | 1.9 | 25 | OK |
| RP-IU-SF-06 | IU-SF-06 → ODU-30 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 1.21 | 0.5 | 0.0 | 1.9 | 25 | OK |
| RP-IU-SF-07 | IU-SF-07 → ODU-31 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 1.17 | 0.5 | 0.0 | 1.8 | 25 | OK |
| RP-IU-SF-08 | IU-SF-08 → ODU-32 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 2.91 | 0.5 | 0.0 | 3.8 | 25 | OK |
| RP-IU-SF-09 | IU-SF-09 → ODU-33 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 4.09 | 0.5 | 0.0 | 5.1 | 25 | OK |
| RP-IU-SF-10 | IU-SF-10 → ODU-34 | 5.3 kW | 6.35 / 12.7 (1/4" / 1/2") | 6.05 | 7.5 | 18.75 | 35.5 | 50 | OK |
| RP-IU-SF-11 | IU-SF-11 → ODU-35 | 5.3 kW | 6.35 / 12.7 (1/4" / 1/2") | 5.91 | 7.5 | 21.25 | 38.1 | 50 | OK |
| RP-IU-SF-12 | IU-SF-12 → ODU-36 | 5.3 kW | 6.35 / 12.7 (1/4" / 1/2") | 6.1 | 7.5 | 24.76 | 42.2 | 50 | OK |
| RP-IU-SF-13 | IU-SF-13 → ODU-37 | 5.3 kW | 6.35 / 12.7 (1/4" / 1/2") | 5.98 | 7.5 | 21.79 | 38.8 | 50 | OK |
| RP-IU-TF-01 | IU-TF-01 → ODU-38 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 1.29 | 0.5 | 0.0 | 2.0 | 25 | OK |
| RP-IU-TF-02 | IU-TF-02 → ODU-39 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 1.27 | 0.5 | 0.0 | 2.0 | 25 | OK |
| RP-IU-TF-03 | IU-TF-03 → ODU-40 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 1.19 | 0.5 | 0.0 | 1.9 | 25 | OK |
| RP-IU-TF-04 | IU-TF-04 → ODU-41 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 1.18 | 0.5 | 0.0 | 1.9 | 25 | OK |
| RP-IU-TF-05 | IU-TF-05 → ODU-42 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 1.21 | 0.5 | 0.0 | 1.9 | 25 | OK |
| RP-IU-TF-06 | IU-TF-06 → ODU-43 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 1.17 | 0.5 | 0.0 | 1.8 | 25 | OK |
| RP-IU-TF-07 | IU-TF-07 → ODU-44 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 1.29 | 0.5 | 0.0 | 2.0 | 25 | OK |
| RP-IU-TF-08 | IU-TF-08 → ODU-45 | 2.6 kW | 6.35 / 9.52 (1/4" / 3/8") | 1.31 | 0.5 | 0.0 | 2.0 | 25 | OK |
| RP-IU-TF-09 | IU-TF-09 → ODU-46 | 5.3 kW | 6.35 / 12.7 (1/4" / 1/2") | 6.09 | 4.5 | 10.31 | 23.0 | 50 | OK |
| RP-IU-TF-10 | IU-TF-10 → ODU-47 | 5.3 kW | 6.35 / 12.7 (1/4" / 1/2") | 6.1 | 4.5 | 1.4 | 13.2 | 50 | OK |
| RP-IU-TF-11 | IU-TF-11 → ODU-48 | 5.3 kW | 6.35 / 12.7 (1/4" / 1/2") | 6.16 | 4.5 | 12.29 | 25.2 | 50 | OK |
| RP-IU-TF-12 | IU-TF-12 → ODU-49 | 5.3 kW | 6.35 / 12.7 (1/4" / 1/2") | 6.15 | 4.5 | 13.88 | 27.0 | 50 | OK |

Code reference: SBC 501 Ch.11 §1107 (refrigerant piping); ASHRAE 15; manufacturer piping tables

## 7.3 Condensate drains

| Run | Unit | To | Code min mm | Design mm | Length m | Slope % |
| --- | --- | --- | --- | --- | --- | --- |
| CD-IU-GF-01 | IU-GF-01 | GF-04 KITCHEN (floor drain / waste stack with trap) | 20 | 25 | 4.51 | 1.0 |
| CD-IU-GF-02 | IU-GF-02 | GF-37 KITCHEN (floor drain / waste stack with trap) | 20 | 25 | 6.23 | 1.0 |
| CD-IU-GF-03 | IU-GF-03 | GF-36 BATH (floor drain / waste stack with trap) | 20 | 25 | 3.42 | 1.0 |
| CD-IU-GF-04 | IU-GF-04 | GF-19 WC (floor drain / waste stack with trap) | 20 | 25 | 4.8 | 1.0 |
| CD-IU-GF-05 | IU-GF-05 | GF-21 WC (floor drain / waste stack with trap) | 20 | 25 | 5.35 | 1.0 |
| CD-IU-GF-06 | IU-GF-06 | GF-17 KITCHEN (floor drain / waste stack with trap) | 20 | 25 | 4.86 | 1.0 |
| CD-IU-GF-07 | IU-GF-07 | GF-23 KITCHEN (floor drain / waste stack with trap) | 20 | 25 | 4.57 | 1.0 |
| CD-IU-GF-08 | IU-GF-08 | GF-34 WC (floor drain / waste stack with trap) | 20 | 25 | 5.66 | 1.0 |
| CD-IU-GF-09 | IU-GF-09 | GF-18 BATH (floor drain / waste stack with trap) | 20 | 25 | 3.76 | 1.0 |
| CD-IU-GF-10 | IU-GF-10 | GF-22 BATH (floor drain / waste stack with trap) | 20 | 25 | 3.76 | 1.0 |
| CD-IU-GF-11 | IU-GF-11 | GF-05 BATH (floor drain / waste stack with trap) | 20 | 25 | 2.55 | 1.0 |
| CD-IU-GF-12 | IU-GF-12 | GF-09 BATH (floor drain / waste stack with trap) | 20 | 25 | 2.56 | 1.0 |
| CD-IU-FF-01 | IU-FF-01 | FF-07 KITCHEN (floor drain / waste stack with trap) | 20 | 25 | 3.22 | 1.0 |
| CD-IU-FF-02 | IU-FF-02 | FF-13 KITCHEN (floor drain / waste stack with trap) | 20 | 25 | 4.4 | 1.0 |
| CD-IU-FF-03 | IU-FF-03 | FF-09 WC (floor drain / waste stack with trap) | 20 | 25 | 5.66 | 1.0 |
| CD-IU-FF-04 | IU-FF-04 | FF-11 WC (floor drain / waste stack with trap) | 20 | 25 | 4.85 | 1.0 |
| CD-IU-FF-05 | IU-FF-05 | FF-20 WC (floor drain / waste stack with trap) | 20 | 25 | 4.23 | 1.0 |
| CD-IU-FF-06 | IU-FF-06 | FF-22 WC (floor drain / waste stack with trap) | 20 | 25 | 5.39 | 1.0 |
| CD-IU-FF-07 | IU-FF-07 | FF-18 KITCHEN (floor drain / waste stack with trap) | 20 | 25 | 4.41 | 1.0 |
| CD-IU-FF-08 | IU-FF-08 | FF-24 KITCHEN (floor drain / waste stack with trap) | 20 | 25 | 3.27 | 1.0 |
| CD-IU-FF-09 | IU-FF-09 | FF-08 BATH (floor drain / waste stack with trap) | 20 | 25 | 3.73 | 1.0 |
| CD-IU-FF-10 | IU-FF-10 | FF-12 BATH (floor drain / waste stack with trap) | 20 | 25 | 3.76 | 1.0 |
| CD-IU-FF-11 | IU-FF-11 | FF-19 BATH (floor drain / waste stack with trap) | 20 | 25 | 3.75 | 1.0 |
| CD-IU-FF-12 | IU-FF-12 | FF-23 BATH (floor drain / waste stack with trap) | 20 | 25 | 3.77 | 1.0 |
| CD-IU-SF-01 | IU-SF-01 | SF-05 KITCHEN (floor drain / waste stack with trap) | 20 | 25 | 3.67 | 1.0 |
| CD-IU-SF-02 | IU-SF-02 | SF-11 KITCHEN (floor drain / waste stack with trap) | 20 | 25 | 5.73 | 1.0 |
| CD-IU-SF-03 | IU-SF-03 | SF-12 KITCHEN (floor drain / waste stack with trap) | 20 | 25 | 3.43 | 1.0 |
| CD-IU-SF-04 | IU-SF-04 | SF-13 WC (floor drain / waste stack with trap) | 20 | 25 | 6.13 | 1.0 |
| CD-IU-SF-05 | IU-SF-05 | SF-14 WC (floor drain / waste stack with trap) | 20 | 25 | 4.83 | 1.0 |
| CD-IU-SF-06 | IU-SF-06 | SF-20 WC (floor drain / waste stack with trap) | 20 | 25 | 4.81 | 1.0 |
| CD-IU-SF-07 | IU-SF-07 | SF-21 WC (floor drain / waste stack with trap) | 20 | 25 | 6.12 | 1.0 |
| CD-IU-SF-08 | IU-SF-08 | SF-23 KITCHEN (floor drain / waste stack with trap) | 20 | 25 | 4.98 | 1.0 |
| CD-IU-SF-09 | IU-SF-09 | SF-29 KITCHEN (floor drain / waste stack with trap) | 20 | 25 | 3.7 | 1.0 |
| CD-IU-SF-10 | IU-SF-10 | SF-07 BATH (floor drain / waste stack with trap) | 20 | 25 | 4.5 | 1.0 |
| CD-IU-SF-11 | IU-SF-11 | SF-09 BATH (floor drain / waste stack with trap) | 20 | 25 | 4.35 | 1.0 |
| CD-IU-SF-12 | IU-SF-12 | SF-25 BATH (floor drain / waste stack with trap) | 20 | 25 | 4.5 | 1.0 |
| CD-IU-SF-13 | IU-SF-13 | SF-27 BATH (floor drain / waste stack with trap) | 20 | 25 | 4.36 | 1.0 |
| CD-IU-TF-01 | IU-TF-01 | TF-07 KITCHEN (floor drain / waste stack with trap) | 20 | 25 | 5.08 | 1.0 |
| CD-IU-TF-02 | IU-TF-02 | TF-13 KITCHEN (floor drain / waste stack with trap) | 20 | 25 | 6.48 | 1.0 |
| CD-IU-TF-03 | IU-TF-03 | TF-14 WC (floor drain / waste stack with trap) | 20 | 25 | 6.13 | 1.0 |
| CD-IU-TF-04 | IU-TF-04 | TF-15 WC (floor drain / waste stack with trap) | 20 | 25 | 4.84 | 1.0 |
| CD-IU-TF-05 | IU-TF-05 | TF-19 WC (floor drain / waste stack with trap) | 20 | 25 | 4.81 | 1.0 |
| CD-IU-TF-06 | IU-TF-06 | TF-20 WC (floor drain / waste stack with trap) | 20 | 25 | 6.12 | 1.0 |
| CD-IU-TF-07 | IU-TF-07 | TF-22 KITCHEN (floor drain / waste stack with trap) | 20 | 25 | 6.6 | 1.0 |
| CD-IU-TF-08 | IU-TF-08 | TF-28 KITCHEN (floor drain / waste stack with trap) | 20 | 25 | 4.94 | 1.0 |
| CD-IU-TF-09 | IU-TF-09 | TF-09 BATH (floor drain / waste stack with trap) | 20 | 25 | 4.54 | 1.0 |
| CD-IU-TF-10 | IU-TF-10 | TF-11 BATH (floor drain / waste stack with trap) | 20 | 25 | 4.55 | 1.0 |
| CD-IU-TF-11 | IU-TF-11 | TF-24 BATH (floor drain / waste stack with trap) | 20 | 25 | 4.56 | 1.0 |
| CD-IU-TF-12 | IU-TF-12 | TF-26 BATH (floor drain / waste stack with trap) | 20 | 25 | 4.55 | 1.0 |

Code reference: SBC 501 §307.2.1 (disposal), §307.2.2 Table 307.2.2 (drain size), slope >= 1 %

# 8. Design checks

| Check | Status | Detail |
| --- | --- | --- |
| Every room served | PASS | 49 conditioned rooms served, 52 exhaust rooms; not served by design (stores/shafts): GF-01, GF-07, GF-10, GF-12, GF-13, GF-16, GF-20, GF-28, GF-29, GF-30, GF-35, GF-39, GF-40, GF-41, FF-01, FF-02, FF-10, FF-21, FF-29, FF-30, SF-01, SF-02, SF-08, SF-18, SF-26, SF-32, SF-33, SF-34, SF-35, SF-36, SF-37, TF-01, TF-02, TF-03, TF-04, TF-10, TF-25, TF-31, TF-32, TF-33, TF-34 |
| No duct crossing shaft/stair/column unresolved | PASS | trunk routes chosen clear of shafts, stairs (not served) and columns; beams not on plan - coordinate |
| Airflows balance | PASS | supply = unit airflow in all ducted zones; building OA 891.3 L/s vs exhaust 1725.0 L/s (net -834 L/s) |
| All items tagged (unique) | PASS | 400 tags |
| Every drawing item in BOQ | PASS | 465 drawn tags all in BOQ (pipe runs 49 measured by size in section G) |
| Unit external static pressure | PASS | all ducted units have ESP margin |
| Refrigerant length / height limits | PASS | within generic limits (verify with brand) |
| Diffuser noise (NC) | PASS | all diffusers at or below room NC target |
| Fresh-air fraction | PASS | OA fraction within limit for untreated fresh air |
| Open questions | PASS | none |

# 9. Code clause register

| Rule | Clause applied |
| --- | --- |
| design_conditions | SBC 602 §302 / SBC 601 §302.1 (design conditions); ASHRAE Fundamentals 2021 Ch.14 (0.4 % cooling, 99.6 % heating) |
| envelope_u | SBC 602 Ch.4 prescriptive envelope table / SBC 601 Ch.5 (max U-factor, SHGC) |
| load_method | ASHRAE Fundamentals 1997 Ch.28 CLTD/SCL/CLF method, Tables 30-36 |
| infiltration | ASHRAE Fundamentals 2021 Ch.16 §'Residential air change method' |
| internal_gains | ASHRAE Fundamentals 2021 Ch.18 Table 1 (people), Tables 2-3 (lighting), Tables 5-9 (equipment) |
| oa_rate | SBC 501 §403.3.1.1 & Table 403.3.1.1; ASHRAE 62.1-2019 §6.2.2.1 Eq.6-1, Table 6-1 |
| oa_zone_eff | ASHRAE 62.1-2019 §6.2.2.2 Table 6-2 (Ez) |
| oa_system_eff | ASHRAE 62.1-2019 §6.2.4.3.1 simplified procedure (Ev) |
| exhaust_toilet | SBC 501 Table 403.3.1.1 (toilet rooms, private dwellings: 25 L/s intermittent or 10 L/s continuous) |
| exhaust_kitchen | SBC 501 Table 403.3.1.1 (kitchens, private dwellings: 50 L/s intermittent or 12 L/s continuous) |
| exhaust_toilet_public | ASHRAE 62.1-2019 Table 6-4 (toilet public: 25 L/s per WC/urinal) |
| duct_sizing | ASHRAE Fundamentals 2021 Ch.21 (equal friction method, Eq.18-19 Altshul-Tsal) |
| duct_construction | SBC 501 §603.4 metallic ducts; SMACNA 2005 Tables 2-1/2-2 (gauge) |
| duct_insulation | SBC 601 §C403.11.1 / ASHRAE 90.1-2019 §6.4.4.1.2, Table 6.8.2 |
| pipe_insulation | SBC 601 §C403.11.3 / ASHRAE 90.1-2019 §6.4.4.1.3, Table 6.8.3-1/-2 |
| refrigerant_piping | SBC 501 Ch.11 §1107 (refrigerant piping); ASHRAE 15; manufacturer piping tables |
| chw_piping | ASHRAE Fundamentals 2021 Ch.22 (water velocity / friction limits) |
| condensate | SBC 501 §307.2.1 (disposal), §307.2.2 Table 307.2.2 (drain size), slope >= 1 % |
| equipment_efficiency | SASO 2663 / SBC 601 Table C403.3.2 minimum efficiency |
| noise | ASHRAE Applications 2019 Ch.49 Table 1 (design NC) |
| safety_factor | Designer allowance - not a code requirement |
| controls | SBC 601 §C403.4 / ASHRAE 90.1 §6.4.3 (thermostatic controls, OA damper shut-off) |

# Appendix - sample sheet (M-101)